## Burugupally (hidden)
Line From | To | Bearing | Is it new or exists | Material | Length in Mtrs | House Holds | Cum Households | Pop 2011 | Ultimate Population | Demand in Liters @ 100 lpcd | Demand in LPM | Dia required | Provide Dia in MM | Head loss per 1000m | Net head loss in m | HGL @ begin | HGL @ end | GL @ end | Residual head in m | Static Head | Velocity m/sec | Class of Pipe
O | O1 |  | New | PVC | 12 |  | 152 | 532 | 782 | 78200 | 325.8333 | 108.8 | 140 | 1.377 | 0.02 | 474 | 473.98 | 463 | 10.98 | 13.98 | 0.43119 | 6 Kg/cm2
O1 | A |  | New | PVC | 305 | 35 | 35 | 122.5 | 180 | 18000 | 75 | 55.4 | 90 | 0.807 | 0.25 | 473.98 | 473.73 | 464 | 9.73 | 12.98 | 0.21788 | 6 Kg/cm2
O1 | D |  | Exist | PVC | 40 | 7 | 117 | 409.5 | 601 | 60100 | 250.4167 | 96.4 | 140 | 0.855 | 0.03 | 473.98 | 473.95 | 463 | 10.95 | 13.98 | 0.27737 | 6 Kg/cm2
D | B |  | New | PVC | 75 | 18 | 110 | 385 | 565 | 56500 | 235.4167 | 93.7 | 110 | 2.438 | 0.18 | 473.95 | 473.77 | 462 | 11.77 | 14.98 | 0.45009 | 6 Kg/cm2
B | B1 |  | New | PVC | 177 | 42 | 92 | 322 | 473 | 47300 | 197.0833 | 86.4 | 110 | 1.768 | 0.31 | 473.77 | 473.46 | 461 | 12.46 | 15.98 | 0.37818 | 6 Kg/cm2
B1 | B2 |  | New | PVC | 150 | 32 | 32 | 112 | 164 | 16400 | 68.3333 | 53.1 | 90 | 0.682 | 0.1 | 473.46 | 473.36 | 460 | 13.36 | 16.98 | 0.19437 | 6 Kg/cm2
B1 | C |  | Exist | PVC | 85 | 18 | 18 | 63 | 92 | 9200 | 38.3333 | 40.7 | 75 | 0.576 | 0.05 | 473.46 | 473.41 | 459 | 14.41 | 17.98 | 0.1609 | 6 Kg/cm2

## Revised rates(SSR 2015-16) (hidden)
Month | 25.07.2015 | SSR 2015-16 |  | JUNE
H2=HR Plates (1.6&2mm -Avg) | 44500 | BWSC Pipes
W2=Wire Rods (5.5/6mm ) | 42500 | Class | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200
C2=Cement | 6300 | 12 | 3272 | 3964 | 4350 | 4804 | 5370 | 7077 | 8534 | 9700 | 11990 | 13540 | 19402 | 21457
|  | 14 | 3272 | 3964 | 4350 | 4820 | 5435 | 7178 | 8745 | 10462 | 12481 | 14809 | 19754 | 22098
|  | 16 | 3272 | 3964 | 4372 | 4892 | 5514 | 7284 | 9331 | 11188 | 13416 | 15870 | 19948 | 22904
|  | 18 | 3272 | 3984 | 4435 | 4949 | 5775 | 7701 | 9899 | 11895 | 14340 | 16931 | 21877 | 25209
|  | 20 | 3272 | 4022 | 4483 | 5188 | 6054 | 8112 | 10464 | 12643 | 15231 | 18056 | 24046 | 27687
|  | 22 | 3316 | 4064 | 4688 | 5397 | 6344 | 8458 | 11058 | 13616 | 15979 | 19667 | 25573 | 29898
|  | 24 | 3403 | 4166 | 4871 | 5645 | 6649 | 8909 | 11820 | 14414 | 17601 | 21498 | 28334 | 32472
|  | 26 | 3528 | 4313 | 5057 | 5861 | 6911 | 9316 | 12309 | 15508 | 18834 | 23002 | 29840 | 33761
|  | 28 | 3594 | 4437 | 5236 | 6096 | 7371 | 9891 | 12906 | 16250 | 19730 | 24248 | 31800 | 37739
|  | 30 | 3783 | 4637 | 5912 | 6619 | 7842 | 10405 | 13744 | 17286 | 21080 | 25997 | 34611 | 41561
| Pig iron | Dia | K9-SSR Rates | Revised-K9 | K7 SSR Rates | K7 Revised
| 26000 | 100 | 1062 | 1062 | 892 | 892
|  | 150 | 1569 | 1569 | 1235 | 1235
|  | 200 | 2095 | 2095 | 1722 | 1722
|  | 250 | 2749 | 2749 | 2310 | 2310
|  | 300 | 3482 | 3482 | 2967 | 2967
|  | 350 | 4340 | 4340 | 3734 | 3734
|  | 400 | 5233 | 5233 | 4532 | 4532
|  | 450 | 6261 | 6261 | 5452 | 5452
|  | 500 | 7284 | 7284 | 6498 | 6498
|  | 600 | 9607 | 9607 | 8647 | 8647
|  | 700 | 12420 | 12420 | 11189 | 11189
|  | 750 | 13938 | 13938 | 12537 | 12537
|  | 800 | 15380 | 15380 | 13855 | 13855
|  | 900 | 18758 | 18758 | 16904 | 16904
|  | 1000 | 22235 | 22235 | 20036 | 20036
|  | 1100 | 23747 | 23747
|  | 1200 | 27765 | 27765
HT Wire | 59500 | PSC Pipes
Cement | 6300 | Dia | 6 Kg/cm2 | 8 Kg/cm2 | 10 Kg/cm2 | 12 Kg/cm2 | 14 Kg/cm2 | 16 Kg/cm2
|  | 350 | 2901 | 2911 | 2925 | 2941 | 3001 | 3104
|  | 400 | 3121 | 3144 | 3179 | 3222 | 3282 | 3332
|  | 450 | 3338 | 3355 | 3394 | 3461 | 3549 | 3625
|  | 500 | 3613 | 3630 | 3660 | 3741 | 3819 | 3931
|  | 600 | 4156 | 4188 | 4233 | 4366 | 4505 | 4642
|  | 700 | 5094 | 5118 | 5201 | 5326 | 5513 | 5671
|  | 800 | 6014 | 6078 | 6235 | 6385 | 6638 | 6875
|  | 900 | 6977 | 7034 | 7194 | 7493 | 7783 | 8308
|  | 1000 | 8192 | 8267 | 8501 | 8838 | 9251 | 9735
|  | 1100 | 9307 | 9444 | 9708 | 10231 | 10680 | 11179
|  | 1200 | 10335 | 10514 | 11052 | 11554 | 12215 | 13179
|  | 1300 | 11724 | 12372 | 13034 | 13706 | 14859 | 16190
|  | 1400 | 13368 | 14117 | 14900 | 16152 | 17443 | 18363
|  | 1500 | 15575 | 16459 | 17343 | 18782 | 20219 | 21265
|  | 1600 | 17533 | 18542 | 19552 | 22097 | 22877 | 24061
|  | 1700 | 18461 | 19200 | 20201 | 22678 | 25066 | 26461
|  | 1800 | 19973 | 21233 | 22406 | 24592 | 27172 | 28687
|  | 1900 | 21328 | 22494 | 24485 | 25879 | 28114 | 31475
|  | 2000 | 23457 | 24906 | 26232 | 28786 | 32730 | 35283
| Cement | AC Pipes |  |  |  |  | AC -Couplings
| 6300 | Dia | Class - 15 | Class - 20 | Class - 25 |  | Class - 15 | Class - 20 | Class - 25
| Fiber | 80 | 198 | 218 | 271 |  | 92 | 99 | 114
| 75500 | 100 | 261 | 332 | 408 |  | 119 | 129 | 155
|  | 125 | 340 | 424 | 532 |  | 149 | 165 | 199
|  | 150 | 478 | 596 | 749 |  | 175 | 219 | 270
|  | 200 | 791 | 1015 | 1287 |  | 321 | 354 | 450
|  | 250 | 1002 | 1303 | 1631 |  | 376 | 475 | 604
|  | 300 | 1402 | 1830 | 2339 |  | 490 | 637 | 819
|  | 350 | 1708 | 2221 | 2803 |  | 635 | 820 | 1046
|  | 400 | 2219 | 2906 | 3607 |  | 978 | 1277 | 1632
|  | 450 | 2641 | 3508 | 4391 |  | 1171 | 1544 | 1979
|  | 500 | 3255 | 4287 | 5382 |  | 1396 | 1866 | 2381
|  | 600 | 4631 | 6052 | 7711 |  | 1725 | 2170 | 2776
|  | 700 | 6085 | 8255 | 10674 |  | 2266 | 3050 | 3966
|  | 750 | 6935 | 9529 | 12213 |  | 2556 | 3494 | 4509
|  | 800 | 7935 | 10796 | 13856 |  | 2899 | 3931 | 5087
|  | 850 | 8901 | 12145 | 15602 |  | 3230 | 4397 | 5702
|  | 900 | 9923 | 13569 | 17452 |  | 3574 | 4888 | 6347
|  | 1000 | 12249 | 16658 | 21461 |  | 4362 | 5944 | 7746
| Pig Iron | CI Pipes
| 26000 | Dia | LA | A | B
|  | 80 | 834 | 904 | 972
|  | 100 | 1015 | 1115 | 1191
|  | 125 | 1279 | 1396 | 1504
|  | 150 | 1549 | 1697 | 1829
|  | 200 | 2261 | 2454 | 2656
|  | 250 | 3047 | 3318 | 3590
|  | 300 | 3929 | 4298 | 4655
|  | 350 | 5026 | 5453 | 5915
|  | 400 | 6120 | 6687 | 7217
|  | 450 | 7405 | 8136 | 8775
|  | 500 | 8758 | 9541 | 10322
|  | 600 | 11581 | 12643 | 13693
|  | 700 | 15246 | 16657 | 17996
|  | 750 | 17076 | 18670 | 20254
|  | 800 | 19114 | 20827 | 22530
|  | 900 | 23293 | 29103 | 27538
|  | 1000 | 27985 | 30568 | 33040
| Resin | HDPE-80 Grade
| 111770 | Class PE-80 | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450 | 500 | 560 | 630 | 710
|  | 4 | 90 | 122 | 175 | 261 | 337 | 416 | 544 | 687 | 842 | 1093 | 1352 | 1685 | 2141 | 2610 | 3382 | 4300 | 5281 | 6539 | 8271 | 10510
| Resin | HDPE-100 Grade
| 112600 | Class PE-100 | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450 | 500 | 560 | 630 | 710
|  | 6 | 105 | 149 | 212 | 318 | 406 | 510 | 667 | 839 | 1037 | 1338 | 1646 | 2063 | 2615 | 3284 | 4319 | 5371 | 6644 | 7759 | 9785 | 12443
|  | 8 | 134 | 190 | 271 | 404 | 521 | 652 | 849 | 1074 | 1327 | 1711 | 2114 | 2646 | 3351 | 4201 | 5520 | 6893 | 8499 | 9935 | 12570 | 15931
|  | 10 | 162 | 229 | 325 | 482 | 626 | 784 | 1021 | 1293 | 1594 | 2059 | 2542 | 3178 | 4029 | 5059 | 6632 | 8293 | 10231 | 11889 | 15061 | 19130
|  | 12.5 | 212 | 302 | 429 | 645 | 827 | 1041 | 1356 | 1712 | 2120 | 2675 | 3302 | 4149 | 5232 | 6655 | 8617 | 10894 | 13454 | 15185 | 18071
| Resin | PVC Pipe rates
| 71214 | Class | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315
2.5
|  | 4 | 53 | 78 | 106 | 154 | 201 | 251 | 331 | 422 | 513 | 682 | 793 | 1038 | 1314
|  | 6 | 77 | 105 | 152 | 220 | 281 | 362 | 469 | 604 | 735 | 985 | 1209 | 1527 | 1919
|  | 10 | 116 | 168 | 237 | 354 | 462 | 573 | 751 | 962 | 1171 | 1567 | 1907 | 2413 | 3046
|  | GRP Pipes | Not given
Hoop Glass | 82 | Dia | 3 | 6 | 9 | 12 | 15 | Note:Not Revised, Do not use (Only SSR rates)
Choop Glass | 78 | 300 | 0 | 0 | 0 | 0 | 0
Resin | 110 | 350 | 0 | 0 | 0 | 0 | 0
|  | 400 | 0 | 0 | 0 | 0 | 0
|  | 450 | 0 | 0 | 0 | 0 | 0
|  | 500 | 0 | 0 | 0 | 0 | 0
|  | 600 | 0 | 0 | 0 | 0 | 0
|  | 700 | 0 | 0 | 0 | 0 | 0
|  | 800 | 0 | 0 | 0 | 0 | 0
|  | 900 | 0 | 0 | 0 | 0 | 0
|  | 1000 | 0 | 0 | 0 | 0 | 0
HT Wire | 59500 | PCCP Pipes
Cement | 6300 | Dia | 4kg/cm2 | 6 Kg/cm2 | 8 Kg/cm2 | 10 Kg/cm2 | 12 Kg/cm2 | 14 Kg/cm2 | 16 Kg/cm2 | 18kg/cm2 | 20kg/cm2
HR coil | 44500 | 400 | 5299 | 5299 | 5299 | 5299 | 5326 | 5383 | 5479 | 5570 | 5640
|  | 450 | 5760 | 5760 | 5760 | 5787 | 5856 | 5940 | 6061 | 6144 | 6240
|  | 500 | 6297 | 6297 | 6311 | 6401 | 6477 | 6583 | 6682 | 6831 | 6941
|  | 600 | 7490 | 7546 | 7646 | 7779 | 7902 | 8026 | 8216 | 8392 | 8570
|  | 700 | 8658 | 8795 | 8960 | 9135 | 9301 | 9462 | 9665 | 9924 | 10118
|  | 800 | 10175 | 10366 | 10596 | 10826 | 11036 | 11250 | 11512 | 11788 | 12106
|  | 900 | 12064 | 12308 | 12593 | 12880 | 13167 | 13425 | 13773 | 14117 | 14460
|  | 1000 | 13990 | 14317 | 14660 | 15015 | 15367 | 15660 | 16067 | 16487 | 16919
|  | 1100 | 15571 | 15960 | 16373 | 16745 | 17137 | 17495 | 17942 | 18413 | 19446
|  | 1200 | 17661 | 18115 | 18576 | 19035 | 19506 | 19927 | 20449 | 21483 | 22221
|  | 1300 | 19663 | 20189 | 20724 | 21260 | 21810 | 22294 | 23529 | 24187 | 25014
|  | 1400 | 21578 | 22176 | 22801 | 23428 | 24052 | 25287 | 26053 | 26835 | 28573
|  | 1500 | 23698 | 24365 | 25034 | 25692 | 27075 | 27835 | 28983 | 30690 | 32692
|  | 1600 | 26725 | 27468 | 28227 | 29643 | 30505 | 31367 | 33513 | 34466 | 35392
|  | 1700 | 28791 | 29652 | 30564 | 32187 | 33163 | 34989 | 36634 | 37666 | 38643
|  | 1800 | 31566 | 32470 | 34239 | 35336 | 36407 | 38420 | 40175 | 41414 | 42653
|  | 1900 | 36864 | 37895 | 39868 | 41033 | 43117 | 44774 | 46395 | 47771 | 49071
|  | 2000 | 39362 | 41316 | 42641 | 44004 | 46383 | 47823 | 50049 | 51630 | 53033

## CI specials (hidden)
|  | Rate per Kg as per SSR |  |  | #REF!
| Pig iron-SSR |  | #REF!
| Coke-SSR |  | #REF!
| Prsent Pig iron Cost |  | 0
| Present Coke Cost |  | 0
Weight of Double Flanged CI pipes as per 7181 : 1986 (Table 2)
0.6 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 0.6 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 11.88 | 3.7 | 7.4 | 19.28 | #REF! | #REF! | #REF! | 15.58 | #REF! | #REF!
2 | 100 | 25.4 | 15.24 | 4.2 | 8.4 | 23.64 | #REF! | #REF! | #REF! | 19.44 | #REF! | #REF!
3 | 125 | 33.1 | 19.86 | 5.3 | 10.6 | 30.46 | #REF! | #REF! | #REF! | 25.16 | #REF! | #REF!
4 | 150 | 41.6 | 24.96 | 6.7 | 13.4 | 38.36 | #REF! | #REF! | #REF! | 31.66 | #REF! | #REF!
5 | 200 | 60.1 | 36.06 | 9.3 | 18.6 | 54.66 | #REF! | #REF! | #REF! | 45.36 | #REF! | #REF!
6 | 250 | 81.8 | 49.08 | 12 | 24 | 73.08 | #REF! | #REF! | #REF! | 61.08 | #REF! | #REF!
7 | 300 | 106.1 | 63.66 | 14.8 | 29.6 | 93.26 | #REF! | #REF! | #REF! | 78.46 | #REF! | #REF!
8 | 350 | 133.5 | 80.1 | 19 | 38 | 118.1 | #REF! | #REF! | #REF! | 99.1 | #REF! | #REF!
9 | 400 | 162.6 | 97.56 | 23.4 | 46.8 | 144.36 | #REF! | #REF! | #REF! | 120.96 | #REF! | #REF!
10 | 450 | 197 | 118.2 | 26.5 | 53 | 171.2 | #REF! | #REF! | #REF! | 144.7 | #REF! | #REF!
11 | 500 | 229.3 | 137.58 | 32.1 | 64.2 | 201.78 | #REF! | #REF! | #REF! | 169.68 | #REF! | #REF!
12 | 600 | 306.5 | 183.9 | 44 | 88 | 271.9 | #REF! | #REF! | #REF! | 227.9 | #REF! | #REF!
0.9 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 0.9 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 17.82 | 3.7 | 7.4 | 25.22 | #REF! | #REF! | #REF! | 21.52 | #REF! | #REF!
2 | 100 | 25.4 | 22.86 | 4.2 | 8.4 | 31.26 | #REF! | #REF! | #REF! | 27.06 | #REF! | #REF!
3 | 125 | 33.1 | 29.79 | 5.3 | 10.6 | 40.39 | #REF! | #REF! | #REF! | 35.09 | #REF! | #REF!
4 | 150 | 41.6 | 37.44 | 6.7 | 13.4 | 50.84 | #REF! | #REF! | #REF! | 44.14 | #REF! | #REF!
5 | 200 | 60.1 | 54.09 | 9.3 | 18.6 | 72.69 | #REF! | #REF! | #REF! | 63.39 | #REF! | #REF!
6 | 250 | 81.8 | 73.62 | 12 | 24 | 97.62 | #REF! | #REF! | #REF! | 85.62 | #REF! | #REF!
7 | 300 | 106.1 | 95.49 | 14.8 | 29.6 | 125.09 | #REF! | #REF! | #REF! | 110.29 | #REF! | #REF!
8 | 350 | 133.5 | 120.15 | 19 | 38 | 158.15 | #REF! | #REF! | #REF! | 139.15 | #REF! | #REF!
9 | 400 | 162.6 | 146.34 | 23.4 | 46.8 | 193.14 | #REF! | #REF! | #REF! | 169.74 | #REF! | #REF!
10 | 450 | 197 | 177.3 | 26.5 | 53 | 230.3 | #REF! | #REF! | #REF! | 203.8 | #REF! | #REF!
11 | 500 | 229.3 | 206.37 | 32.1 | 64.2 | 270.57 | #REF! | #REF! | #REF! | 238.47 | #REF! | #REF!
12 | 600 | 306.5 | 275.85 | 44 | 88 | 363.85 | #REF! | #REF! | #REF! | 319.85 | #REF! | #REF!
1.0 mtrs Length | [9 empty] | tail piece
Sno. | Dia | Wt. of 1m length | wt. of 1.0 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost | wt | rate | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 80 | 19.8 | 19.8 | 3.7 | 7.4 | 27.2 | #REF! | #REF! | #REF! | 23.5 | #REF! | #REF!
2 | 100 | 25.4 | 25.4 | 4.2 | 8.4 | 33.8 | #REF! | #REF! | #REF! | 29.6 | #REF! | #REF!
3 | 125 | 33.1 | 33.1 | 5.3 | 10.6 | 43.7 | #REF! | #REF! | #REF! | 38.4 | #REF! | #REF!
4 | 150 | 41.6 | 41.6 | 6.7 | 13.4 | 55 | #REF! | #REF! | #REF! | 48.3 | #REF! | #REF!
5 | 200 | 60.1 | 60.1 | 9.3 | 18.6 | 78.7 | #REF! | #REF! | #REF! | 69.4 | #REF! | #REF!
6 | 250 | 81.8 | 81.8 | 12 | 24 | 105.8 | #REF! | #REF! | #REF! | 93.8 | #REF! | #REF!
7 | 300 | 106.1 | 106.1 | 14.8 | 29.6 | 135.7 | #REF! | #REF! | #REF! | 120.9 | #REF! | #REF!
8 | 350 | 133.5 | 133.5 | 19 | 38 | 171.5 | #REF! | #REF! | #REF! | 152.5 | #REF! | #REF!
9 | 400 | 162.6 | 162.6 | 23.4 | 46.8 | 209.4 | #REF! | #REF! | #REF! | 186 | #REF! | #REF!
10 | 450 | 197 | 197 | 26.5 | 53 | 250 | #REF! | #REF! | #REF! | 223.5 | #REF! | #REF!
11 | 500 | 229.3 | 229.3 | 32.1 | 64.2 | 293.5 | #REF! | #REF! | #REF! | 261.4 | #REF! | #REF!
12 | 600 | 306.5 | 306.5 | 44 | 88 | 394.5 | #REF! | #REF! | #REF! | 350.5 | #REF! | #REF!
2.0 mtrs Length
Sno. | Dia | Wt. of 1m length | wt. of 2.0 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 39.6 | 3.7 | 7.4 | 47 | #REF! | #REF! | #REF!
2 | 100 | 25.4 | 50.8 | 4.2 | 8.4 | 59.2 | #REF! | #REF! | #REF!
3 | 125 | 33.1 | 66.2 | 5.3 | 10.6 | 76.8 | #REF! | #REF! | #REF!
4 | 150 | 41.6 | 83.2 | 6.7 | 13.4 | 96.6 | #REF! | #REF! | #REF!
5 | 200 | 60.1 | 120.2 | 9.3 | 18.6 | 138.8 | #REF! | #REF! | #REF!
6 | 250 | 81.8 | 163.6 | 12 | 24 | 187.6 | #REF! | #REF! | #REF!
7 | 300 | 106.1 | 212.2 | 14.8 | 29.6 | 241.8 | #REF! | #REF! | #REF!
8 | 350 | 133.5 | 267 | 19 | 38 | 305 | #REF! | #REF! | #REF!
9 | 400 | 162.6 | 325.2 | 23.4 | 46.8 | 372 | #REF! | #REF! | #REF!
10 | 450 | 197 | 394 | 26.5 | 53 | 447 | #REF! | #REF! | #REF!
11 | 500 | 229.3 | 458.6 | 32.1 | 64.2 | 522.8 | #REF! | #REF! | #REF!
12 | 600 | 306.5 | 613 | 44 | 88 | 701 | #REF! | #REF! | #REF!
2.75 mtrs Length
Sno. | Dia | Wt. of 1m length | wt. of 2.75 m length | Wt. of one flange | wt. of double flange | Total wt. | rate per Kg | Amount | Revised cost
mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 80 | 19.8 | 54.45 | 3.7 | 7.4 | 61.85 | #REF! | #REF! | #REF!
2 | 100 | 25.4 | 69.85 | 4.2 | 8.4 | 78.25 | #REF! | #REF! | #REF!
3 | 125 | 33.1 | 91.025 | 5.3 | 10.6 | 101.625 | #REF! | #REF! | #REF!
4 | 150 | 41.6 | 114.4 | 6.7 | 13.4 | 127.8 | #REF! | #REF! | #REF!
5 | 200 | 60.1 | 165.275 | 9.3 | 18.6 | 183.875 | #REF! | #REF! | #REF!
6 | 250 | 81.8 | 224.95 | 12 | 24 | 248.95 | #REF! | #REF! | #REF!
7 | 300 | 106.1 | 291.775 | 14.8 | 29.6 | 321.375 | #REF! | #REF! | #REF!
8 | 350 | 133.5 | 367.125 | 19 | 38 | 405.125 | #REF! | #REF! | #REF!
9 | 400 | 162.6 | 447.15 | 23.4 | 46.8 | 493.95 | #REF! | #REF! | #REF!
10 | 450 | 197 | 541.75 | 26.5 | 53 | 594.75 | #REF! | #REF! | #REF!
11 | 500 | 229.3 | 630.575 | 32.1 | 64.2 | 694.775 | #REF! | #REF! | #REF!
12 | 600 | 306.5 | 842.875 | 44 | 88 | 930.875 | #REF! | #REF! | #REF!
Rates of various materials-With Price Variation
| Size | 2m d/f | .9 d/f | .6 d/f | bellmouth | 90 bend | tpiece | DuFbend | semicir | DI D/F Gate valves With 5% Extra for Conveyance-PN1.6
| 80 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 100 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 125 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 150 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 250 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 300 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 350 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 450 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
| 500 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
| 600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
Weight of Double Flanged CI Bends as per IS : 1538 : 1993 (Table 21& 23)
Double Flanged 90 deg Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 13 |  | #REF! | #REF! | #REF!
| 2 | 100 | 17 |  | #REF! | #REF! | #REF!
| 3 | 125 | 23 |  | #REF! | #REF! | #REF!
| 4 | 150 | 31 |  | #REF! | #REF! | #REF!
| 5 | 200 | 49 |  | #REF! | #REF! | #REF!
| 6 | 250 | 72 |  | #REF! | #REF! | #REF!
| 7 | 300 | 100 |  | #REF! | #REF! | #REF!
| 8 | 350 | 137 |  | #REF! | #REF! | #REF!
| 9 | 400 | 181 |  | #REF! | #REF! | #REF!
| 10 | 450 | 226 |  | #REF! | #REF! | #REF!
| 11 | 500 | 290 |  | #REF! | #REF! | #REF!
| 12 | 600 | 442 |  | #REF! | #REF! | #REF!
Double Flanged 45 deg Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 14 |  | #REF! | #REF! | #REF!
| 2 | 100 | 18 |  | #REF! | #REF! | #REF!
| 3 | 125 | 25 |  | #REF! | #REF! | #REF!
| 4 | 150 | 34 |  | #REF! | #REF! | #REF!
| 5 | 200 | 54 |  | #REF! | #REF! | #REF!
| 6 | 250 | 80 |  | #REF! | #REF! | #REF!
| 7 | 300 | 112 |  | #REF! | #REF! | #REF!
| 8 | 350 | 115 |  | #REF! | #REF! | #REF!
| 9 | 400 | 149 |  | #REF! | #REF! | #REF!
| 10 | 450 | 185 |  | #REF! | #REF! | #REF!
| 11 | 500 | 231 |  | #REF! | #REF! | #REF!
| 12 | 600 | 342 |  | #REF! | #REF! | #REF!
Weight of Duck Foot Bends as per IS : 1538 : 1993 (Table 22)
Duck Foot Bend
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 21 |  | #REF! | #REF! | #REF!
| 2 | 100 | 26 |  | #REF! | #REF! | #REF!
| 3 | 125 | 36 |  | #REF! | #REF! | #REF!
| 4 | 150 | 47 |  | #REF! | #REF! | #REF!
| 5 | 200 | 74 |  | #REF! | #REF! | #REF!
| 6 | 250 | 111 |  | #REF! | #REF! | #REF!
| 7 | 300 | 156 |  | #REF! | #REF! | #REF!
| 8 | 350 | 214 |  | #REF! | #REF! | #REF!
| 9 | 400 | 281 |  | #REF! | #REF! | #REF!
| 10 | 450 | 350 |  | #REF! | #REF! | #REF!
| 11 | 500 | 446 |  | #REF! | #REF! | #REF!
| 12 | 600 | 667 |  | #REF! | #REF! | #REF!
Weight of Bell Mouth Pieces as per IS : 1538 : 1993 (Table 20)
Bell Mouth
| Sno. | Dia | Wt. of bell mouth in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 7 |  | #REF! | #REF! | #REF!
| 2 | 100 | 9 |  | #REF! | #REF! | #REF!
| 3 | 125 | 12 |  | #REF! | #REF! | #REF!
| 4 | 150 | 15 |  | #REF! | #REF! | #REF!
| 5 | 200 | 23 |  | #REF! | #REF! | #REF!
| 6 | 250 | 31 |  | #REF! | #REF! | #REF!
| 7 | 300 | 45 |  | #REF! | #REF! | #REF!
| 8 | 350 | 58 |  | #REF! | #REF! | #REF!
| 9 | 400 | 80 |  | #REF! | #REF! | #REF!
| 10 | 450 | 93 |  | #REF! | #REF! | #REF!
| 11 | 500 | 120 |  | #REF! | #REF! | #REF!
| 12 | 600 | 201 |  | #REF! | #REF! | #REF!
Semi Circular Bends
| Sno. | Dia | Wt. in |  | rate per Kg | Amount | Revised cost
|  | mm | Kg/ Pc
| 1 | 2 | 3 |  | 8 | 9 | 10
| 1 | 80 | 25 |  | #REF! | #REF! | #REF!
| 2 | 100 | 35 |  | #REF! | #REF! | #REF!
| 3 | 125 | 45 |  | #REF! | #REF! | #REF!
| 4 | 150 | 65 |  | #REF! | #REF! | #REF!
| 5 | 200 | 100 |  | #REF! | #REF! | #REF!
| 6 | 250 | 160 |  | #REF! | #REF! | #REF!
| 7 | 300 | 210 |  | #REF! | #REF! | #REF!
| 8 | 350 | 340 |  | #REF! | #REF! | #REF!
| 9 | 400 | 275 |  | #REF! | #REF! | #REF!
| 10 | 500 |  |  |  |  | #REF!
| 10 | 600 |  |  |  |  | #REF!

## Tap data (hidden)
Rate analysis for Proposed house service connections
A) | Providing 15mm dia House Service Connection as per standard specification including the cost of the materials like Clamp Saddle,Ferrule Tapping Saddle confirming to I.S stadard manufactured from virgin resin of PE-80 , Compression Elbows, MDPE PE100 Pipe including lowering, laying and jointing including earth work excavation and refilling the pipe line trench after laying the pipe line and including cost of 15mm dia meter of BIS standard and construction of meter chamber etc complete as directed by departmental officer for finished item of work.
6
1 | Providing and fixing Ferrule Tapping Saddle confirming to I.S standard , Manufactured from virgin resin of PE-80/PE-100 having blue/black colour using food grade compounded raw material with quality assurance certificate from quality agencie s like DVGMK/ KIWA/SPGN/WRc etc. for usage in drinking water system and having working pressure of 10 Bar. The cost shall include testing of all materials, labour all taxes etc complete 100* 15mm size rate as per PH S.oR page no.56
| 1 | No |  | 837 | 1 | Each | 837
2 | Cost of 15mm dia pipe line MDPE pipe including all fittings rate as per lowest quotation
| 6 | mts |  | 25 | 1 | mts | 150
3 |  |  | Trench size | 0.3 | * | 0.6
Earthwork excavation for pipe line
| 1.08 | Cum |  | #REF! | 1 | Cum | #REF!
4 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. BMW-B-06 BUILD
| 1 | No |  | 1200 | 1 | No | 1200
5 | Laying, jointing of MDPE/HDPE pipes as per BIS No.7634 part-III and BIS No.7634 part-II/75 for HDPE pipes.
| 6 | mts |  | 20 | 1 | mts | 120
|  | Add labour allowance @ |  |  |  | 20% | 24
#REF!
6 |  | Add over heads @ 14 |  |  |  | 14% | #REF!
[6 empty] | Rs | #REF!
7 |  |  | Add for VAT @ 5% and labour cess @ 1% |  |  | 0% | #REF!
[6 empty] | Total Rs. | #REF! | /Each
[6 empty] | Say Rs. | #REF! | /Each

## Pipe Line Data (hidden)
DATA SHEET FOR LAYING AND JOINTING OF PVC / HDPE PIPES
#REF! | #REF! |  | SOR | 2015-2016
#REF! | Name of work :- |  | INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
Earth work excuvation for pipeline trench of the specified size, lowering and laying of PVC pipes, jointing the pipes with each other and with the specials, testing the pipeline with water of required pressure, refilling the trench with excuvated soils watering and tamping etc,.
#REF! | PART - I |  | #REF!
| Earthwork Excavation in all types of soils including refilling by Manual means 1/2 |  |  |  | 112.84 | /1cum | 56.42
| Earthwork Excavation in all types of soils including refilling by Machine 1/2 |  |  |  | 81.28 | /1cum | 40.64
|  |  |  | Average Rate |  |  | 97.06 | /1cum
PART - II
FOR 63 AND 75 MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 120% for narrow trench |  |  |  | 116.47
[5 empty] | 213.53 | /1cum
| With trench size 0.50 X 0.75m |  |  | 0.50 X 0.75 X | 213.53 |  | 80.07 | /1m
| Dia | Trench charge | L & J | #REF! | #REF! |  | #REF! | Total
PVC | 63mm | 80.07 | 6.24 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 75mm | 80.07 | 7.43 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 63mm | 80.07 | 37 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 75mm | 80.07 | 41 | #REF! | #REF! |  | #REF! | #REF! | /1m
FOR 90MM TO 140MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
| With trench size 0.70 X 1.00m |  |  | 0.70 X 1.00 X | 169.85 |  | 118.89 | /1m
| Dia | Trench charge | L & J | VAT @ % | #REF! |  | #REF! | Total
PVC | 90mm | 118.89 | 8.91 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 110mm | 118.89 | 10.89 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 125mm | 118.89 | 12.38 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 140mm | 118.89 | 13.86 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 90mm | 118.89 | 46 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 110mm | 118.89 | 53 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 125mm | 118.89 | 64 |  |  |  | #REF! | #REF! | /1m
HDPE | 140mm | 118.89 | 67 | #REF! | #REF! |  | #REF! | #REF! | /1m
| With trench size 0.80 X 1.10m |  |  | 0.80 X 1.10 X | 169.85 |  | 149.46 | /1m
| Dia | Trench charge |  | L & J | #REF! | #REF! |  | Total
PVC | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
PVC | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
FOR 160MM TO 200MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
| With trench size 0.80 X 1.10m |  |  | 0.80 X 1.10 X | 169.85 |  | 149.46 | /1m
| Dia | Trench charge | L & J | VAT @ HDPE% | #REF! |  | #REF! | Total
PVC | 160mm | 149.46 | 15.84 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 180mm | 149.46 | 17.82 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 200mm | 149.46 | 19.8 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 160mm | 149.46 | 72 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 180mm | 149.46 | 80 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 200mm | 149.46 | 87 | #REF! | #REF! |  | #REF! | #REF! | /1m
| With trench size 0.80 X 1.10m |  |  | 0.80 X 1.10 X | 169.85 |  | 149.46 | /1m
| Dia | Trench charge |  | L & J | #REF! | #REF! |  | Total
PVC | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
PVC | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
FOR 200MM TO 315MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
| With trench size 0.90 X 1.20m |  |  | 0.90 X 1.20 X | 169.85 |  | 183.43 | /1m
| Dia | Trench charge | L & J | VAT @ HDPE% | #REF! |  | #REF! | Total
PVC | 225mm | 183.43 | 22.28 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 250mm | 183.43 | 24.75 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 280mm | 183.43 | 27.72 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 315mm | 183.43 | 31.19 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 225mm | 183.43 | 96 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 250mm | 183.43 | 102 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 280mm | 183.43 | 112 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 315mm | 183.43 | 183 | #REF! | #REF! |  | #REF! | #REF! | /1m
| Asst. Engineer |  |  | #REF!
| RWS Thirumalagir |  |  | RWS Subdivision Thungathurthy
Note on A2: Turn Over Tax Percentage
Note on A3: Sundries Operator

## HDPE DATA CC (hidden)
- for HDPE pipes
[9 empty] | #REF! | #REF! | #REF!
| HDPE PE80 Raw material : |  | #REF! | (excluding CED) |  | Cost of specials : |  | 0.5
| HDPE PE100 Raw material : |  | #REF! | (excluding CED)
Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE 'filling with excavated soils including laying jointing testing of pipe line including cost of materials etc. complete
| HDPE PE 80 Class | 4
| Trench size |  | 0.70 x 1.00m | [5 empty] | 0.80 x1.10m |  |  | 0.90 x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm | 450mm
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4467
2 | Cost of specials (0.50%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 22.335
3 | Earthwork,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost f pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| HDPE PE 100 Class | 6
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80mx1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm | 450mm
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 5565
2 | Cost of specials (0.50%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 27.825
3 | Earthwork,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
`
| HDPE PE 100 Class | 8
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80mx1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm | 450mm
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7144 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Cost of specials (0.50%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 35.72
3 | Earthwork,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost of Pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| HDPE PE 100 Class | 10
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm | 450mm
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 8597
2 | Cost of specials (0.50%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 42.985
3 | Earthwork,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost of Pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| HDPE PE 100 Class | 12.5
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm | 450mm | 500mm
A) Materials component
| Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost of specials (0.50%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Earthwork,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 8597 | 0
| Cost of Pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Input (hidden)
Name of The work | INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M) | Intra village system for Providing Drinking water
Name Of The Mandal | THIRUMALAGIRI
Name Of The GP | THATIPAMULA
Name Of The Hab | THATIPAMULA
Population
ST | 0
SC | 1186
Plain | 2032
Total | 3218
Existing Faicilities
Capacity OHSR KL | 90
No of House Holds | 805

## Cover Page (hidden)
Sub Estimate for Intra village Net work (For Hab wise)
Name Of The Habitation | : | THATIPAMULA
Name Of The Gram Panchaythi | : | THATIPAMULA
Mandal | : | THIRUMALAGIRI
Est Cost In Lakhs | : | #N/A

## Specification (hidden)
SPECIFICATION REPORT ACCOMPNYING THE ESTIMATE FOR
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
Executive summary
The proposed (Intra Village Network) Single Village Scheme is located in THATIPAMULA H/O THATIPAMULA of THIRUMALAGIRI Mandal of Nalgonda Dist.The present source for the habitations in mandal depends on Ground water only
Scope of TDWSP
The Telangana Drinking Water Project plans to provide protected potable drinking water to all the Habitations in the state, with rate of supply of 100 LPCD to Rural Habitations, 135 LPCD to Urban Municipalities, 150 LPCD to Urban Municipal Corporations and 10% provision made towards Industrial demand by linking up a number of water resources on Godavari and Krishna basins. This project is proposed to build a world’s largest water supply project plan in the state. The project aim is to supply drinking water needs of all the towns and villages in the Telangana state. The proposed TELANGANA DRINKING WATER PROJECT pipeline would have 5,227 kms of main trunk line, 45,809 kms of secondary network and 75,000 kms of distributary network. The proposed Secondary Grid - Thirumalagiri Segment of Telangana Drinking Water Supply Project pipeline would have 150 kms of secondary network and covering the habitations in Thirumalagir(M) in Thungathurthy Assembly Constitiencies of Nalgonda District.
Methodology
The proposed (Intra Village supply Network) is formulated for Construction of Service reservoirs and laying of Distribution lines from the existing and new proposed structures in the Village to cover all the House Holds. The water supply upto the existing structure in the village are to be provided under Thirumalagiri Segment of Telangana Drinking Water Supply Project.
I) | Details of Population as Per 2011
| ST | 0
| SC | 1186
| Plain | 2032
| Total | 3218
II | Details of Infrastructure Existing/New Items Required As per 100 LPCD
S No | Zone Number | Item | Unit(No/KL/RMT) | Total Requirment | Exsiting |  | Damaged /Condemned |  | Balance Required/Proposed in this proposal
[5 empty] | No | Total Qty | No | Total Qty | No | Total Qty
I | Storage Reservior
OHBR
GLBR
1 | 1 | OHSR | KL | 198.725 | 1 | 90 |  |  | 2 | 100
GLSR
Other If any Speicify
|  | Total |  | 198.725 | 1 | 90 | 0 | 0 | 2 | 100 |  |  | 0
II | Pipe lines/Distibution Network
DI
|  | HDPE | [6 empty] | 1 | 2500
1 | 1 | PVC | RMT | 8412 | 1 | 5912 |  | 0 |  |  | Exist | Replace
GI
Other If any Speicify
|  | Total |  | 8412 | 1 | 5912 | 0 | 0 | 1 | 2500
IV | Details of House hold connections
Sno | Zone No If Any | Localities covered | Total House hold existing in Hab | Number of House connections already existing and requires furrel provision | Balance New House connections required | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 1 | Village | 805 | 0 | 805
Scheme Cost
The Total cost of the Intra Village Grid in Thirumalagir is Rs. 1623 Lakhs. The Habitation is proposed to covered by construction of OHSR's & laying of distribution pipe lines with households ferrule connections. The estimate is prepared with common SSR 2015-16.
Project Period
The implementation period is tentatively proposed is in the year 2018.
Conclusion
By implementing this Intra Village water supply scheme, it can be ensured availability of 100 LPCD quantity of drinking water of good quality on long-term basis. The long-term objectives of improvement of health of the people in the mandal result in the overall development in the proposed Habitations.
| Asst. Engineer |  |  |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  |  |  | RWS&S Circle Nalgonda

## Design (hidden)
DESIGN CALCULATIONS FOR THATIPAMULA VILLAGE OF THIRUMALAGIRI (M)
Habitations covered with the scheme
Sno | Habitation | Population as per 2001 census |  |  | Remarks
1 | Population 2011 | 3218
2 | Day School
| UPS | 0
| PS | 126
| ZPHS | 184
| Anganwadi | 0
310
3 | Boarding schools
| KPVGB | 0
| SWR | 0
| Model Schools | 0
0
4 | Hospital
0
5 | Hostels
0
6 | Offices
0
7 | Restaurants
0
8 | Hotels
0
9 | Industries
0
| Total | 3218 |  |  | 161
1 | Prospective demand calculations
| Population to be served as per 2011 | 3218
| Present Population : Growth in 14 Years | 3218 | X | 1.1495 | 3699 | 2025
| Ultimate population (22 years) | 3218 | X | (1.008)22 | 3835
| LPCD Proposed | 100
| Prospective Demand @ 100 LPCD | 3835 | X | 100 | 383500 | Ltrs
| Demand for Day Schools | 310 | X | 45 | 13950 | Ltrs
| Demand for Boarding schools | 0 | X | 45 | 0 | Ltrs
| Demand for Hospital | 0 | X | 340 | 0 | Ltrs
| Demand for Hostels | 0 | X | 135 | 0 | Ltrs
| Demand for Hotels | 0 | X | 180 | 0 | Ltrs
| Demand for Industries | 0 | X | 30 | 0 | Ltrs
|  |  |  | Total | 397450 | Ltrs
3 | Existing Facilities
| Capacity of existing OHSR | 90000
4 | Service reservoir calculations
| No of Filling proposed |  |  |  | 2
| Capacity required ( Prospective demand with one / Two filling ) |  |  |  | 198725 | Ltrs
| Capacity of Existing OHSR |  |  |  | 90000 | Ltrs
| Net capacity of OHSR required |  |  |  | 108725 | Ltrs | 69900
| Hence provide | 100000 |  | litres capacity OHSR
| Asst. Engineer | Dy. Exe Engineer
| RWS & S Thirumalagiri | RWS Subdivision Thungathurthy
| Executive Engineer | Superintending Engineer
| RWS&S Div-I Nalgonda | RWS&S Circle Nalgonda

## Spec (hidden)
SPECIFICATION REPORT ACCOMPNYING THE ESTIMATE FOR
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
Grant :TDWSP Est Cost In Lakhs
#N/A
Administratively sanctioned for of Thirumalagir Mandal Vide GO RT No 668, Dated: 27-10-2015 of Panchaythi Raj and Rural Development (RWS-IV) Department
The Population of THATIPAMULA H/O THATIPAMULA Village as per census 2011 is 3218 and 90 KL OHSR is working By utilising the existing facilities estimate is prepared for the additional items. Existing pipelines are proposed to be used as far as possible where ever the proper sizes are available
As such the estimate is prepared with following provisions.
1 | Construction of OHSR
2 | Providing Distribution pipelines
3 | House Service Connection
4 | Labour Cess @ 1%
5 | Value added Tax @ 3.5%
6 | LS for Unforeseen items
#N/A
Assistant Executive Engineer Deputy Executive Engineer
RWS Thirumalagir RWS Subdivision Thungathurthy
Note on B8: Press Ctrl Shft B for listing of Specifications

## Abstract (hidden)
TELANGANA DRINKING WTAER SUPPLY PROJECT
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M) | [6 empty] | #REF! | 20 | 30 | 40 | 50 | 60 | 70 | 100 | 120
ABSTRACT ETIMATE | [7 empty] | 44.31 | 43.53 | 39.22 | 35.95 | 29.76 | 26.09 | 27.47 | 27.92
S.No | Description | Qty | Rate | per | Amount
1 | Construction of 40 KL & 60KL OHSRs with 12 mtr Staging |  |  |  | #N/A |  |  |  |  | `
2 | Laying of Pipe Line |  |  |  | #REF!
3 | VAT @ 5% |  |  |  | #N/A
4 | CESS @ 1% |  |  |  | #N/A
5 | NAC @0.1% |  |  |  | #N/A
6 | QC @ .5% |  |  |  | #N/A
7 | LS for Unforceen |  |  |  | 37408
|  |  |  | Total | #N/A
#N/A
| Asst. Engineer |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  | RWS Subdivision Thungathurthy
| Executive Engineer |  | Superintending Engineer |  |  | VAT | 5
| RWS&S Div-I Nalgonda |  | RWS&S Circle Nalgonda |  |  | CESS | 1
[6 empty] | Price Varartion | 5%
[6 empty] | Wapcos | 0.2%
[6 empty] | VAT | 5
[6 empty] | CESS | 1
[6 empty] | Price Varartion | 5%
[6 empty] | Wapcos | 0.2%
[6 empty] | NAC | 0.1%
Note on D4: Staging: Enter any required staging.

## Pipe line (hidden)
Sub Estimate
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
S.No | Description of item | No. | L | B | D | Qty | Unit | Rate | Per | Amount
1 | 'Construction of pipe line for water supply with PVC pipes as per IS:4984/1988,with its amendments and revisons thereon including supplying of pipes, specials as per requirements, lowering, laying and jointing of pipe lines true to alighnment and gradient, trench excavtion for pipe lines in all soils except Rock requiring blasting and refilling trenches with excavated earth(other than rocky soil and boulders) with watering, tamping and removeing surplus earth from site of work and filling pipe line with water and testing etc., complete. The rates are inclusive of cost,conveyance of all materials and labour charges for finished item of pipe line work and Excluding all Taxes. | [13 empty] | Total | THATIPAMULA | SREERAM THANDA | NANDAPURAM | EDULAPARRE THANDA | RAMUNIBANDA THANDA | THIRUMALAGIRI | NELLI BANDA THANDA | THONDA | VELISHALA | RAVI CHERU THANDA | MARRIKUNTA THANDA | CHINTALA KUNTA THANDA | RUPLA THANDA | BOOKYA THANDA | BOOLGADA THANDA | MAMIDALA | KOKYA THANDA | LAKYA THANDA | HEMLA THANDA | KOTHA CHEKRU THANDA | EDULABODU THANDA | DEVA THANDA | JALALPURAM | RAJNAIK THANDA | KOTYA THANDA | ISLAVATH THANDA | GULLABANDA THANDA | JETHYA NAIK THANDA | THUMMALAKUNTA THANDA | RAGHAVAPURAM | RAGHAVAPURAM THANDA | SIDDISAMUDRAM | MONDICHINTA THANDA | BHUKYA PANTHULU THANDA | RUPLA THANDA | JATOTHU THANDA | GUNDEPURI | CHOUDLA THANDA | KANNAREDDY KUNTA THANDA | SALEGUDEM THANDA | BOOKYA THANDA H/O GUNDEPURI | BANDLAPALLY | DUBBA THANDA | MALIPURAM | MAMIDIPALLI | HARI CHANDRU THANDA | PANIGIRI | LAXMAN THANDA | ETOOR | PRAGATHI NAGAR | ANANTHARAM | KOTHA THANDA
| 63 mm PVC6 Kg | 1X1 | 210 |  |  | 210 | Rmt | #REF! | Rmt | #REF! | 190.2785 | 80.17 | 63 | New | #REF! | 210 | 200 | 90 | 3160 | 250 | 1025 | 520 | 150 | 350 | 100 | 0 | 196 | 100 | 200 | 100 | 50 | 0 | 264 | 0 | 70 | 1600 | 200 | 0 | 150 | 0 | 0 | 0 | 250 | 100 | 0 | 196 | 220 | 250 | 200 | 1350 | 60 | 50 | 0 | 0 | 400 | 80 | 850 | 570 | 100 | 2845 | 0 | 185 | 0 | 1170 | 150 | #REF! | #REF!
| 75 mm PVC6 Kg | 1X1 | 180 |  |  | 180 | Rmt | #REF! | Rmt | #REF! | 223.5371 | 109.39 | 75 | New | #REF! | 180 | 260 | 90 | 5650 | 250 | 575 | 1350 | 0 | 150 | 150 | 100 | 100 | 100 | 590 | 0 | 100 | 150 | 100 | 100 | 140 | 1100 | 200 | 150 | 100 | 150 | 150 | 273 | 150 | 0 | 200 | 150 | 150 | 100 | 0 | 250 | 100 | 0 | 0 | 150 | 0 | 0 | 660 | 160 | 0 | 2810 | 100 | 355 | 0 | 120 | 100 | #REF! | #REF!
| 90 mm PVC6 Kg | 1X1 | 1300 |  |  | 1300 | Rmt | #REF! | Rmt | #REF! | 278.8217 | 158.28 | 90 | New | #REF! | 1300 | 0 | 0 | 770 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 150 | 0 | 200 | 100 | 530 | 200 | 0 | 1760 | 0 | 0 | 100 | 800 | 0 | #REF! | #REF!
| 110 mm PVC6 Kg | 1X1 | 660 |  |  | 660 | Rmt | #REF! | Rmt | #REF! | 358.613 | 229.05 | 110 | New | #REF! | 660 | 0 | 0 | 645 | 0 | 2750 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 240 | 0 | 610 | 460 | 0 | 215 | 0 | 0 | 0 | 390 | 0 | #REF! | #REF!
| 125 mm PVC6 Kg | 1X1 | 150 |  |  | 150 | Rmt | #REF! | Rmt | #REF! | 429.7646 | 292.94 | 125 | New | #REF! | 150 | 0 | 0 | 3110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 200 | 0 | 0 | 0 | #REF! | #REF!
| 140 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 523.9233 | 376.82 | 140 | New | #REF! | 0 | 0 | 0 | 2430 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360 | 0 | 625 | 0 | 0 | 0 | #REF! | #REF!
| 160 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 672.7522 | 488.08 | 160 | New | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 180 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 829.0041 | 628.42 | 180 | New | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 200 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 980.5419 | 765.2 | 200 | New | #REF! | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 225 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 1296.3142 | 1022.93 | 225 | New | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 250 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 1554.6142 | 1256.01 | 250 | New | #REF! | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 280 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 1920.8837 | 1585.99 | 280 | New | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
| 315 mm PVC6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF! | 2371.9546 | 1993.77 | 315 | New | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF!
|  |  | 2500 | [11 empty] | #REF! | 2500 | 460 | 180 | 16965 | 500 | 5080 | 2840 | 150 | 500 | 250 | 100 | 296 | 200 | 1100 | 100 | 150 | 150 | 364 | 100 | 210 | 4110 | 400 | 150 | 250 | 150 | 150 | 273 | 400 | 100 | 200 | 346 | 370 | 350 | 200 | 2460 | 160 | 50 | 150 | 150 | 840 | 180 | 2650 | 1390 | 100 | 9410 | 100 | 1365 | 100 | 2480 | 250 | #REF! | #REF!
2 | Cutting road surface including stacking of excavated materials for pipe line trench Tapping work. For 63 mm to 315 dia Pipe
a | Cutting open B.T.Road surface | 1X1 | 125 | 0.5 | 0.15 | 9 | Cum | 902 | Cum | 8118 | 403.3634
b | Cutting open C.C.Road Surface | 1X1 | 375 | 0.5 | 0.15 | 28 | Cum | 1878 | Cum | 52584 | 436.6221
3 | Supply and delivery and Fixing of DI D/F Gate valves ( soft Seated ) valves conforming to IS 3896-oart 2-1985 wedge fully rubber lined with EPDM food grade quality and the valve should be of vacuum tight and 100% leak proof with face to face dimensions. All the valves should be with Electrostatic powder caoting both insisde and outside pockets body passages.Drilled as per IS: 1538
| 80mm dia on 63mm | 1X6 |  |  |  | 6 | No | #REF! | No | #REF! | 35811.333
| '80mm dia on 75mm | 1X12 |  |  |  | 12 | No | #REF! | No | #REF! | 35855.6429
| '80mm dia on 90mm | 1X4 |  |  |  | 4 | No | #REF! | No | #REF! | 35898.8166
| '100mm dia on 110mm | 1X2 |  |  |  | 2 | No | #REF! | No | #REF! | 47849.9493
| '125mm dia on 125mm | 1X2 |  |  |  | 1 | No | #REF! | No | #REF! | 49284.5932
| '150mm dia on 140mm | 1X2 |  |  |  | 1 | No | #REF! | No | #REF! | 63872.1547
| 150mm dia on 160mm | 1X1 |  |  |  | 0 | No | #REF! | No | #REF! | 63922.1453
| 150mm dia on 180mm | 1X1 |  |  |  | 0 | No | #REF! | No | #REF! | 63984.6336
| 200mm dia on 200mm | 1X1 |  |  |  | 0 | No | #REF! | No | #REF! | 88983.0966
| 250mm dia on 250mm | 1X1 |  |  |  | 0 | No | #REF! | No | #REF! | 89038.768
| 300mm dia on 315mm | 1X1 |  |  |  | 0 | No | #REF! | No | #REF! | 122212.4403
4 | Supply and placing of the Design Mix Concrete corresponding to IS 456 using WEIGH BATCHER / MIXER with 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, for M-30 grade | [9 empty] | 122602.1397
a | B.T.Road surface | 1X1 | 125 | 0.5 | 0.15 | 9 | Cum | 0 | Cum | 0 | 167052.6088
b | C.C.Road Surface | 1X1 | 375 | 0.5 | 0.15 | 28 | Cum | 0 | Cum | 0
5 | Providing 15mm dia House service connection as per standard specification including the cost of the materials like Clamp Saddle/ Electro fusion Saddle confirming to prEN 12201-3, Manufactured from virgin resin of PE-SO/PE-100 with FLOW CONTROL VALVE (5 LPM @5m head), Compression Elbows, MOPE PESO Blue Pipe & Supplying and fixing of of GI Pipe including lowering, laying and jointing including earth work excavation and refilling the pipe line trench after laying the pipe line and including cost of 15mm dia meter brass body CP finish bib tap of BIS standard etc including GI verticals complete for finished item of work
|  | 805 |  |  |  | 805 | Each | 1998 | Each | 1608390
6 | Provision for CED @ 12.36% | [8 empty] | 29947
7 | L.S.for U/S Items | L.S.
[8 empty] | TOTAL |  | #REF! |  |  | 110000 | 130000
| Asst. Engineer | [5 empty] | Dy. Exe Engineer
| RWS & S Thirumalagiri | [5 empty] | RWS Subdivision Thungathurthy
| Executive Engineer | [5 empty] | Superintending Engineer
| RWS&S Div-I Nalgonda | [5 empty] | RWS&S Circle Nalgonda

## OHSR (hidden)
| SUB-ESTIMATE FOR CONSTRUCTION OF |  | 60000 | LITRES CAPACITY OHSR.
|  | VRCC OHSR OF | 12 | MTS. STAGGING. |  |  |  |  | 90000 | 125
S.No | Description |  | Qty |  | Rate |  | per | Amount | 200000 | 200
1 | Construction of OHSR for finished work including 2 coats of snowcem painting,lettering, fixing of all required fixtures, pipes, bends, valves, etc. complete as per departmental designs and drawings.Fixtures include:a) RCC or Aluminium ladder inside 0.60 m wide. b) spiral staircase on the outside shall be provided upto 200KL ELSR. Above 200KL ELSR Capacity dog legged staircase shall be provided with staircase flight width of 1.0mts and landing width of 1.20mts with S.S railing upto 1.0 height. c) Lightening arrestor, including conductor and earthing etc with relevant IS codes. d) RCC ventilators with copper or stainless steel fly proof mesh. e) D.I Manholes frame and cover 0.60 x 0.60 m as per IS specifications (light duty) - 2 Nos. f) Water level indicator of good quality with ebonite/ copper float approved pattern - 1 No. g) The ladder shall be with Aluminium and Verticals with HDPE of 10kg/Sqcm shall be provided for single column OHSRs only. h) Minimum staging for all ELSR/OHSR shall be 12.0mts. i) The increase in staging shall be at 1.0mt interval. j) The railing provided to the gallery and staircase shall be with stainless steel of grade 304 for a height of 1mts k)The railing provided to the gallery and stair case shall be with stainless steel of grade 304 for a height of 1.20mts. l)The dog legged staircase shall be enclosed with brick / CRS wall on three sides and front side with PVC door of standard maker up to 1st brace level from ground level to prevent unauthorized entry. m) D.I swan neck ventilators shall be provided in top dome and slab. M30grade | [8 empty] | Pipe dia
|  |  | 60000 | x | 24.0535 | / per litre = |  | 1443209
2 | DI Specials & Sluice Valves As Per Sub Estimate | [6 empty] | #N/A
3 | Add 13.615 % Contractor Profit | [6 empty] | #N/A
4 | LS for Unforceen
[7 empty] | Total | #N/A
| Asst. Engineer |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda
DATA for construction of OHSR of capacity 60000 Litres with staging of 12 mts & raft foundation
[7 empty] | S.S.R. | 2015-16
1 | Construction of VRCC OHSR as per departmental drawins and specifications, with 12 Mts staging height and with raft footings. And with cement rate of Rs 5500 / MT and steel rate @ Rs 33000 /MT
| Basic rate for OHSR of 60000 Litres | [5 empty] | 23.58 | /1Ltr
| Correction for every metre of staging less than 12 m, the rate shall be reduced by Rs.0.05paise per litre | Less by 12m | 0 | X | 0.05 | = | 0 | /1Ltr
[7 empty] | 23.58 | /1Ltr
2 | Correction for excess cement rate
| Present rate of cement as per SSR | [5 empty] | 5600 | /MT
| Liter rate worked out with cement rate of | [5 empty] | 5500 | /MT
| Difference | [5 empty] | 100 | /MT
| Difference in multiples of 100's | [5 empty] | 1
| With 0.7 % for Rs 100 difference total percentage to be added to the rate |  | 1 | X | 0.7 | = | 0.7 | %
3 | Correction for excess steel rate
| Present rate of steel for reinforcement | [5 empty] | 37000 | /MT
| Liter rate worked out with steel rate of | [5 empty] | 33000 | /MT
| Difference | [5 empty] | 4000 | /MT
| Difference in multiples of 1000 | [5 empty] | 4
| With 2% for Rs 1000 difference , total percentage to be added to the rate |  | 4 | X | 2 | = | 8 | %
4 | Wind Pressure.
| Wind Pressure As Per OHSR Design | [5 empty] | 250 | Kg/Sq.mt.
| Present Calculated Wind Pressure | [5 empty] | 116.16
| Difference | [5 empty] | -133.84
| Decrese in Wind Pressure @ 5% |  | -133.84 | X | 0.05 | = | -6.692
| Initial rate worked out | [5 empty] | 23.58 | /1Ltr
| Correction for cement rate | [5 empty] | 0.16506 | /1Ltr
| Correction of steel rate | [5 empty] | 1.8864 | /1Ltr
| Correction of wind pressure | [5 empty] | -1.578 | /1Ltr
| Excess for Rural Area ( 10% ) | [5 empty] | 0
[5 empty] | Worked out rate per litre. |  | 24.0535 | /1Ltr
| Asst. Engineer |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda
Note on D2: Staging: Enter any required staging.

## OHSR (hidden)
Input data
[5 empty] | OHSR | no
[5 empty] | OHSR Capacity | 100000
[5 empty] | Staging | 12 | #N/A
[5 empty] | Valv Ch 0.90 | #REF!
[5 empty] | Vlav Ch1.05 | #REF!
[5 empty] | Valv Ch1.20 | #REF! |  | B
[5 empty] | Valves 50% add | no |  | FALSE
[5 empty] | Basic rate | #N/A |  | OHSR
[5 empty] | Cement rate | #REF! |  | Inlet | 250
[5 empty] | Steel rate | #REF! |  | Oulet | 250
[5 empty] | PH SSR Cem rate | #REF! |  | Over flow | 250
[5 empty] | PH SSR steel rate | #REF!
|  | 100000 | Lts Capacity OHSR
#REF!
|  | M.W.L | #N/A |  | Free board | 0.15
|  | L.W.L | 12 |  | Dead storge | 0.15
|  | G.L | 0
|  | Inlet pipe | Outlet pipe | Scour pipe | Over flow
| Rec.dia | 250 | 250 | 80 | 250
| 5 Mt pipe | #N/A | 2 | 2 | #N/A
| 1 Mt pipe | #N/A | 2 | 1 | #N/A
| 1 Mt pipe | #N/A | 3 | 3.85 | #N/A
| Duck foot bend | 1 | 1 | 1 | 1
| Tail Piece | 0 | 0 | 0 | 0
| Bell mouth | 1 | 0 | 1 | 1
| 90o D/f bend | 0 | 0 | 0 | 0
| Sluice valve | 1 | 1 | 1 | 0
| Semicircular Bend | 0 | 0 | 1 | 0
upto 350mm dia DI Wafer Butterfly valves and
above 350mm dia DI D/F Butterfly valves
Total
| DI Sp.Cost | #N/A | #N/A | #N/A | #N/A | #N/A
| Butterfly valves Cost DI | #N/A | #N/A | #N/A | #N/A | #N/A
| Wind Velocity | 158.39 | KMPH |  | Velocity | 44 | Pressure | 116.16
Construction of 100000 litres capacity OHSRWith 12.00 Mtrs StagingTHATIPAMULAH/O of THATIPAMULA(V) of THIRUMALAGIRI Mandal
[7 empty] | Est.Cost Rs | #N/A
Construction of 100000 Lts Capacity OHSR with 12 m staging with raft foundation
plastering with CM(1:3) 2 coats of Weather proof emulsion painting for external surfaces, and 3 coats of epoxy paint to inner surface of the reservoir including roof dome, lettering as per Dept Direction, Fixing of the DI D/F Pipes verticals, vlaves, Execution as per Design and drawigns supplied by the Dept., including the cost and conveyance of the all materials but excluding cost of Pipes , Bends , Specials Etc complete including the following.- M30 Grade Concrete
b)D.I man hole covers with frame of size 0.60 X 0.60 mts -2 Nos (light duty)
c) DI Swan Neck ventilators shall be provided in Top dome/slab with flyproof mesh
d)RCC Phinial with copper or Stainless stell flyproof mesh
e)RCC or Aluminium ladder inside of 0.60 mts width
f)RCC spiral stair case with handrailing upto 200kl
for above 200kl capacity Doglegged staircase with flight width of 1mt and landing of 1.2mts and SS Handrailing upto 1mt Thedogleggedstaircaseshallbeenclosedwithbrick/CRSwallonthreesidesandfrontsidewithM.Scollapsiblegateupto1stbracelevel from ground level to prevent unauthorized entry.
g)Waterlevel indicator of good quality with ebonite/copper float approved pattern - 1 No.
h)Lightening arrestor of approved pattern 1 No complete including conductor earthing
J) Railling with Stainless Steel of grade 304 in two rows around OHSR fixed in RCC (1:2:4) of post of size 100x75x75mm with 1.5m m itervals around the pheriphary on top of OHSR
| A) Basic cost | 100000 | X | #N/A |  |  | : Rs | #N/A
| B) | #REF! | [5 empty] | #REF!
C) Add for increse in price of cement
|  | #REF! | #REF! | 0.7 | #N/A |  | : Rs | #REF! | #REF!
( 100 X 100)
D) Add for increase/ Decrease in price of Steel
|  | #REF! | #REF! | 2 | #N/A |  | : Rs | #REF!
( 1000 X 100)
| E) Deduct for staging below 12 Mts by .05 Paise per Lt | [5 empty] | : Rs | 0
F) Add or deduct for Wind Pressure
|  | 116.16 | 250 | 5 | #N/A |  | : Rs | #N/A | #N/A |  | -133.84
|  | ( 100 X 100) | [8 empty] | -669.2 | #REF!
| G) Cost of CI Specials As Per Sub Estimate | [5 empty] | : Rs | #N/A |  |  | -0.06692 | #REF!
#REF!
| H) Cost of Sluice Valves |  |  |  | 3 Nos |  | : Rs | #N/A
| I) Cost of valve chambers |  |  |  | 3 Nos |  | : Rs | #REF! |  |  |  |  | #N/A | Don’t delete
| J) Add Contractor's Profit |  |  |  | #REF! |  |  | #N/A
| K) Provision for unforceen items | [5 empty] | : Rs | 43975
[5 empty] | Total cost |  |  | #N/A | #N/A | DI |  |  |  |  | Dia | Valve Ch rate
|  |  | Rate per lt | #N/A |  |  |  |  | 43975 | LS |  |  |  |  | 1.05 | #REF! | 300
[9 empty] | #N/A | Structure |  |  |  |  | 1.2 | #REF!
Asst. Executive Engineer, | [6 empty] | Dy. Executive Engineer,
TDWSP Sub div Bhongir | [6 empty] | TDWSP Sub div Bhongir
| Executive Engineer, |  |  |  |  | Superintending Engineer
| TDWSP Div Choutuppal |  |  |  |  | TDWSP Circle Hyderabad

## OHSR (2) (hidden)
| SUB-ESTIMATE FOR CONSTRUCTION OF |  | 40000 | LITRES CAPACITY OHSR.
|  | VRCC OHSR OF | 12 | MTS. STAGGING. |  |  |  |  | 90000 | 125
S.No | Description |  | Qty |  | Rate |  | per | Amount | 200000 | 200
1 | Construction of OHSR for finished work including 2 coats of snowcem painting,lettering, fixing of all required fixtures, pipes, bends, valves, etc. complete as per departmental designs and drawings.Fixtures include:a) RCC or Aluminium ladder inside 0.60 m wide. b) spiral staircase on the outside shall be provided upto 200KL ELSR. Above 200KL ELSR Capacity dog legged staircase shall be provided with staircase flight width of 1.0mts and landing width of 1.20mts with S.S railing upto 1.0 height. c) Lightening arrestor, including conductor and earthing etc with relevant IS codes. d) RCC ventilators with copper or stainless steel fly proof mesh. e) D.I Manholes frame and cover 0.60 x 0.60 m as per IS specifications (light duty) - 2 Nos. f) Water level indicator of good quality with ebonite/ copper float approved pattern - 1 No. g) The ladder shall be with Aluminium and Verticals with HDPE of 10kg/Sqcm shall be provided for single column OHSRs only. h) Minimum staging for all ELSR/OHSR shall be 12.0mts. i) The increase in staging shall be at 1.0mt interval. j) The railing provided to the gallery and staircase shall be with stainless steel of grade 304 for a height of 1mts k)The railing provided to the gallery and stair case shall be with stainless steel of grade 304 for a height of 1.20mts. l)The dog legged staircase shall be enclosed with brick / CRS wall on three sides and front side with PVC door of standard maker up to 1st brace level from ground level to prevent unauthorized entry. m) D.I swan neck ventilators shall be provided in top dome and slab. M30grade | [8 empty] | Pipe dia
|  |  | 40000 | x | 35.2234 | / per litre = |  | 1408934
2 | DI Specials & Sluice Valves As Per Sub Estimate | [6 empty] | #N/A
3 | Add 13.615 % Contractor Profit | [6 empty] | #N/A
4 | LS for Unforceen
[7 empty] | Total | #N/A
| Asst. Engineer |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda
DATA for construction of OHSR of capacity 40000 Litres with staging of 12 mts & raft foundation
[7 empty] | S.S.R. | 2015-16
1 | Construction of VRCC OHSR as per departmental drawins and specifications, with 12 Mts staging height and with raft footings. And with cement rate of Rs 5500 / MT and steel rate @ Rs 33000 /MT
| Basic rate for OHSR of 40000 Litres | [5 empty] | 34.53 | /1Ltr
| Correction for every metre of staging less than 12 m, the rate shall be reduced by Rs.0.05paise per litre | Less by 12m | 0 | X | 0.05 | = | 0 | /1Ltr
[7 empty] | 34.53 | /1Ltr
2 | Correction for excess cement rate
| Present rate of cement as per SSR | [5 empty] | 5600 | /MT
| Liter rate worked out with cement rate of | [5 empty] | 5500 | /MT
| Difference | [5 empty] | 100 | /MT
| Difference in multiples of 100's | [5 empty] | 1
| With 0.7 % for Rs 100 difference total percentage to be added to the rate |  | 1 | X | 0.7 | = | 0.7 | %
3 | Correction for excess steel rate
| Present rate of steel for reinforcement | [5 empty] | 37000 | /MT
| Liter rate worked out with steel rate of | [5 empty] | 33000 | /MT
| Difference | [5 empty] | 4000 | /MT
| Difference in multiples of 1000 | [5 empty] | 4
| With 2% for Rs 1000 difference , total percentage to be added to the rate |  | 4 | X | 2 | = | 8 | %
4 | Wind Pressure.
| Wind Pressure As Per OHSR Design | [5 empty] | 250 | Kg/Sq.mt.
| Present Calculated Wind Pressure | [5 empty] | 116.16
| Difference | [5 empty] | -133.84
| Decrese in Wind Pressure @ 5% |  | -133.84 | X | 0.05 | = | -6.692
| Initial rate worked out | [5 empty] | 34.53 | /1Ltr
| Correction for cement rate | [5 empty] | 0.24171 | /1Ltr
| Correction of steel rate | [5 empty] | 2.7624 | /1Ltr
| Correction of wind pressure | [5 empty] | -2.3107 | /1Ltr
| Excess for Rural Area ( 10% ) | [5 empty] | 0
[5 empty] | Worked out rate per litre. |  | 35.2234 | /1Ltr
| Asst. Engineer |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda
Note on D2: Staging: Enter any required staging.

## DI (hidden)
| Requirement of CI Specials |  |  | SSR 2015 - 16 | [5 empty] | Taxes | 1
| Side wall depth | [5 empty] | : | 2.1 | m |  | Rates of various materials
| Staging of the OHSR | [5 empty] | : | 12 | m | Size | 2m d/f | 1m d/f | .6 d/f | bellmouth | 90 bend | tpiece | DuFbend | semicir | sluice valve
| Discharge through inlet pipe |  |  | #N/A |  | 42 | : | 42 | LPM | 80 | #N/A | #N/A | #N/A | #N/A | 956.09 | 1145.85 | #N/A | #N/A | 10418
| Diameter of pipe |  |  |  |  | 80 |  | 80 | mm | 100 | #N/A | #N/A | #N/A | #N/A | 1250.28 | 1429.73 | #N/A | #N/A | 13742
[10 empty] | 125 | 0 | 0 | 0 | 0 | 1691.55 | 1850.41 | 0 | #N/A | 19460
Sub Estimate
Requirement of DI Specials for the OHSR with 12 mtr staging | [9 empty] | 150 | #N/A | #N/A | #N/A | #N/A | 2279.92 | 2328.45 | #N/A | #N/A | 21637
S. No. | Description | Dia. Req | No's | Rate | Per | Amount |  |  |  | 250 | #N/A | #N/A | #N/A | #N/A | 5295.29 | 4492.17 | #N/A | #N/A | 49800
1 | Inlet connections | [8 empty] | 300 | #N/A | #N/A | #N/A | #N/A | 7354.56 | 5770.39 | #N/A | #N/A | 75266
| D/F pipes - 2m. Long | 150 | 7 | #N/A |  | #N/A |  |  |  | 350 | #N/A | #N/A | #N/A | #N/A | 10075.75 | 7288.37 | #N/A | #N/A | 227882
| D/F pipes - 0.90m. Long | 150 | 0 | #N/A |  | #N/A |  |  |  | 400 | #N/A | #N/A | #N/A | #N/A | 13311.76 | 8896.08 | #N/A | #N/A | 239013
| D/F pipes - 0.60m. Long | 150 | 1 | #N/A |  | #N/A |  |  |  | 450 | #N/A | #N/A | #N/A | #N/A | 16621.32 | 10642.06 | #N/A |  | 411203
| 90 D/F bends | 150 | 0 | 2279.92 |  | 0 |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A | 21328.24 | 12479.23 | #N/A |  | 436671
| Tail pieces | 150 | 0 | 2328.45 |  | 0 |  |  |  | 600 | #N/A | #N/A | #N/A | #N/A | 32507.18 | 16761.05 | #N/A |  | 562308
| Duck foot bends | 150 | 1 | #N/A |  | #N/A
[12 empty] | Size | 2m | .9m | .6m
2 | Outlet connections | [8 empty] | Inlet connections |  | 150 | 7 | 0 | 1 | 150
| D/F pipes - 2m. Long | 150 | 6 | #N/A |  | #N/A |  |  |  | Outlet connections |  | 150 | 6 | 0 | 1 | 150
| D/F pipes - 0.90m. Long | 150 | 0 | #N/A |  | #N/A |  |  |  | Scour connections |  | 80 | 6 | 0 | 1 | 80
| D/F pipes - 0.60m. Long | 150 | 1 | #N/A |  | #N/A |  |  |  | Overflow connections |  | 150 | 7 | 0 | 1 | 150
| Bell mouths | 150 | 1 | #N/A |  | #N/A
| Duck foot bends | 150 | 1 | #N/A |  | #N/A | [5 empty] | LPM | Size
[12 empty] | 50 | 80
3 | Scour connections | [10 empty] | 190 | 100 |  | 10 | 80
| D/F pipes - 2m. Long | 80 | 6 | #N/A |  | #N/A | [5 empty] | 300 | 125 |  | 120 | 100
| D/F pipes - 0.90m. Long | 80 | 1 | #N/A |  | #N/A | [5 empty] | 450 | 150 |  | 200 | 150
| D/F pipes - 0.60m. Long | 80 | 3 | #N/A |  | #N/A | [5 empty] | 650 | 200 |  | 300 | 200
| Bell mouths | 80 | 1 | #N/A |  | #N/A | [5 empty] | 1100 | 250 |  | 450 | 250
| Duck foot bends | 80 | 2 | #N/A |  | #N/A | [5 empty] | 1750 | 300
| Semicircular bend | 80 | 1 | #N/A |  | #N/A | [5 empty] | 2500 | 350
[12 empty] | 3500 | 400
4 | Overflow connections | [10 empty] | 4500 | 450
| D/F pipes - 2m. Long | 150 | 7 | #N/A |  | #N/A | [5 empty] | 5700 | 500
| D/F pipes - 0.90m. Long | 150 | 0 | #N/A |  | #N/A | [5 empty] | 7000 | 600
| D/F pipes - 0.60m. Long | 150 | 1 | #N/A |  | #N/A | [5 empty] | 10100 | 700
| Bell mouths | 150 | 1 | #N/A |  | #N/A | [5 empty] | 13700 | 800
| 90 D/F bends | 150 | 0 | 2279.92 |  | 0
| Tail pieces | 150 | 0 | 2328.45 |  | 0
| Duck foot bends | 150 | 1 | #N/A |  | #N/A
5 | Sluice Valves
| Sluice valve for Inlet | 150 | 1 | 21637 | Each | 21637
| Sluice valve for Outlet | 150 | 1 | 21637 | Each | 21637
| Sluice valve for Scour | 80 | 1 | 10418 | Each | 10418 |  | #N/A
| Provision for CED for DI specials |  |  |  |  | #N/A
|  |  | Total |  |  | #N/A
| Asst. Engineer |  |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda

## CI Verticals (hidden)
SUB-ESTIMATE FOR C.I.VERTICALS.
S. NO | Description of item | Measurments | [5 empty] | RATE |  | AMOUNT
|  | No | L | B | D | QTY
1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 8 |  | 9
Requirement of di Specials for the OHSR (UP TO 30 KL) with 12m staging
Inlet
1 | S/D of 80 mm dia 2.00 mtrs long D/Fpipes. | 1x7 | - | - | - | 329 | Kgs
2 | S/D of 80 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 50.44 | Kgs
3 | S/D of 80 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 38.56 | Kgs
4 | S/D of 80 mm dia Duck foot bend. | 1x1 | - | - | - | 21 | Kgs
5 | S/D of 80 mm dia Bell Mouth | 1x1 |  |  |  | 7 | Kgs
Out let
1 | S/D of 80 mm dia 2.00 mtrs long D/Fpipes. | 1x6 | - | - | - | 282 | Kgs
2 | S/D of 80 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 50.44 | Kgs
3 | S/D of 80 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 38.56 | Kgs
4 | S/D of 80 mm dia Duck foot bend. | 1x1 | - | - | - | 21 | Kgs
Scour
6 | S/D of 80 mm dia 2.00 mtrs long D/F pipes. | 1x6 | - | - | - | 282 | Kgs
7 | S/D of 80 mm dia 0.90 mtrs long D/F pipes. | 1x3 |  |  |  | 75.66 | Kgs
8 | S/D of 80 mm dia 0.60 mtrs long D/F pipes. | 1x1 |  |  |  | 19.28 | Kgs
9 | S/D of 80 mm dia Duck Foot Bend. | 1x2 |  |  |  | 42 | Kgs
5 | S/D of 80 mm dia Semicircular Bend | 1x1 | - | - | - | 25 | Kgs
[6 empty] | 1281.94 | Kgs | 73.7 | 1Kg | 94479
10 | Supply and delivery of 80 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
11 | Supply and delivery of 80 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
#REF!
| Add amount of Excise duty payable@ 16 % | [8 empty] | #REF!
| Add amount of Educational cess payable @ 2% | [8 empty] | #REF!
| Add amount of Secondary Higher Educational cess payable @ 1% | [8 empty] | #REF!
#REF!
| Add Vat @ 4 % on Sl.No 1 to 9 only | [8 empty] | 0
| Add Vat @12.5 % on Sl.No 10&11 only Rs. 10425/- | [8 empty] | 0
#REF!
| Add Transportation of valves @ 10% on basic cost. | [8 empty] | 0
[8 empty] | TOTAL Rs. |  | #REF!
Requirement of di Specials for the OHSR (UP TO 40 KL TO 80 KL) with 12m staging
Inlet
1 | S/D of 100 mm dia 2.00 mtrs long D/Fpipes. | 1x7 | - | - | - | 414.4 | Kgs
2 | S/D of 100 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 62.52 | Kgs
3 | S/D of 100 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 47.28 | Kgs
4 | S/D of 100 mm dia Duck foot bend. | 1x1 | - | - | - | 26 | Kgs
5 | S/D of 100 mm dia Bell Mouth | 1x1 |  |  |  | 9 | Kgs
Out let
1 | S/D of 150 mm dia 2.00 mtrs long D/Fpipes. | 1x6 | - | - | - | 579.6 | Kgs
2 | S/D of 150 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 101.68 | Kgs
3 | S/D of 150 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 76.72 | Kgs
4 | S/D of 150 mm dia Duck foot bend. | 1x1 | - | - | - | 47 | Kgs
Scour
6 | S/D of 100 mm dia 2.00 mtrs long D/F pipes. | 1x6 | - | - | - | 355.2 | Kgs
7 | S/D of 100 mm dia 0.90 mtrs long D/F pipes. | 1x3 |  |  |  | 93.78 | Kgs
8 | S/D of 100 mm dia 0.60 mtrs long D/F pipes. | 1x1 |  |  |  | 23.64 | Kgs
9 | S/D of 100 mm dia Duck Foot Bend. | 1x2 |  |  |  | 52 | Kgs
5 | S/D of 100 mm dia Semicircular Bend | 1x1 | - | - | - | 35 | Kgs
[6 empty] | 1923.82 | Kgs | 73.7 | 1Kg | 141786
10 | Supply and delivery of 80 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
11 | Supply and delivery of 100 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
12 | Supply and delivery of 150 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
#REF!
| Add amount of Excise duty payable@ 16 % | [8 empty] | #REF!
| Add amount of Educational cess payable @ 2% | [8 empty] | #REF!
| Add amount of Secondary Higher Educational cess payable @ 1% | [8 empty] | #REF!
#REF!
| Add Vat @ 4 % on Sl.No 1 to 9 only | [8 empty] | 0
| Add Vat @12.5 % on Sl.No 10&11 only Rs. 10425/- | [8 empty] | 0
#REF!
| Add Transportation of valves @ 10% on basic cost. | [8 empty] | 0
[8 empty] | TOTAL Rs. |  | #REF!
Requirement of di Specials for the OHSR (Above 80 KL) with 12m staging
Inlet
1 | S/D of 100 mm dia 2.00 mtrs long D/Fpipes. | 1x7 | - | - | - | 414.4 | Kgs
2 | S/D of 100 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 62.52 | Kgs
3 | S/D of 100 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 47.28 | Kgs
4 | S/D of 100 mm dia Duck foot bend. | 1x1 | - | - | - | 26 | Kgs
5 | S/D of 100 mm dia Bell Mouth | 1x1 |  |  |  | 9 | Kgs
Out let
1 | S/D of 200 mm dia 2.00 mtrs long D/Fpipes. | 1x6 | - | - | - | 832.8 | Kgs
2 | S/D of 200 mm dia0.90 mtrs long D/Fpipes. | 1x2 | - | - | - | 145.38 | Kgs
3 | S/D of 200 mm dia0.60 mtrs long D/Fpipes. | 1x2 | - | - | - | 109.32 | Kgs
4 | S/D of 200 mm dia Duck foot bend. | 1x1 | - | - | - | 74 | Kgs
Scour
6 | S/D of 100 mm dia 2.00 mtrs long D/F pipes. | 1x6 | - | - | - | 355.2 | Kgs
7 | S/D of 100 mm dia 0.90 mtrs long D/F pipes. | 1x3 |  |  |  | 93.78 | Kgs
8 | S/D of 100 mm dia 0.60 mtrs long D/F pipes. | 1x1 |  |  |  | 23.64 | Kgs
9 | S/D of 100 mm dia Duck Foot Bend. | 1x2 |  |  |  | 52 | Kgs
5 | S/D of 100 mm dia Semicircular Bend | 1x1 | - | - | - | 35 | Kgs
[6 empty] | 2280.32 | Kgs | 73.7 | 1Kg | 168060
10 | Supply and delivery of 80 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
11 | Supply and delivery of 100 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
12 | Supply and delivery of 200 mm dia Sluice valve. | 1x1 |  |  |  | 1 | No. | #REF! | Each | #REF!
#REF!
| Add amount of Excise duty payable@ 16 % | [8 empty] | #REF!
| Add amount of Educational cess payable @ 2% | [8 empty] | #REF!
| Add amount of Secondary Higher Educational cess payable @ 1% | [8 empty] | #REF!
#REF!
| Add Vat @ 4 % on Sl.No 1 to 9 only | [8 empty] | 0
| Add Vat @12.5 % on Sl.No 10&11 only Rs. 10425/- | [8 empty] | 0
#REF!
| Add Transportation of valves @ 10% on basic cost. | [8 empty] | 0
[8 empty] | TOTAL Rs. |  | #REF!
| Asst. Engineer | [6 empty] | Dy. Exe Engineer
| RWS & S Thirumalagiri | [6 empty] | RWS Subdivision Thungathurthy

## DI (2) (hidden)
| Requirement of CI Specials |  |  | SSR 2015 - 16 | [5 empty] | Taxes | 1
| Side wall depth | [5 empty] | : | 2.1 | m |  | Rates of various materials
| Staging of the OHSR | [5 empty] | : | 12 | m | Size | 2m d/f | 1m d/f | .6 d/f | bellmouth | 90 bend | tpiece | DuFbend | semicir | sluice valve
| Discharge through inlet pipe |  |  | #N/A |  | 42 | : | 42 | LPM | 80 | #N/A | #N/A | #N/A | #N/A | 956.09 | 1145.85 | #N/A | #N/A | 10418
| Diameter of pipe |  |  |  |  | 80 |  | 80 | mm | 100 | #N/A | #N/A | #N/A | #N/A | 1250.28 | 1429.73 | #N/A | #N/A | 13742
[10 empty] | 125 | 0 | 0 | 0 | 0 | 1691.55 | 1850.41 | 0 | #N/A | 19460
Sub Estimate
Requirement of CI Specials for the OHSR with 12 mtr staging | [9 empty] | 150 | #N/A | #N/A | #N/A | #N/A | 2279.92 | 2328.45 | #N/A | #N/A | 21637
S. No. | Description | Dia. Req | No's | Rate | Per | Amount |  |  |  | 250 | #N/A | #N/A | #N/A | #N/A | 5295.29 | 4492.17 | #N/A | #N/A | 49800
1 | Inlet connections | [8 empty] | 300 | #N/A | #N/A | #N/A | #N/A | 7354.56 | 5770.39 | #N/A | #N/A | 75266
| D/F pipes - 2m. Long | 100 | 7 | #N/A |  | #N/A |  |  |  | 350 | #N/A | #N/A | #N/A | #N/A | 10075.75 | 7288.37 | #N/A | #N/A | 227882
| D/F pipes - 0.90m. Long | 100 | 0 | #N/A |  | #N/A |  |  |  | 400 | #N/A | #N/A | #N/A | #N/A | 13311.76 | 8896.08 | #N/A | #N/A | 239013
| D/F pipes - 0.60m. Long | 100 | 1 | #N/A |  | #N/A |  |  |  | 450 | #N/A | #N/A | #N/A | #N/A | 16621.32 | 10642.06 | #N/A |  | 411203
| 90 D/F bends | 100 | 0 | 1250.28 |  | 0 |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A | 21328.24 | 12479.23 | #N/A |  | 436671
| Tail pieces | 100 | 0 | 1429.73 |  | 0 |  |  |  | 600 | #N/A | #N/A | #N/A | #N/A | 32507.18 | 16761.05 | #N/A |  | 562308
| Duck foot bends | 100 | 1 | #N/A |  | #N/A
[12 empty] | Size | 2m | .9m | .6m
2 | Outlet connections | [8 empty] | Inlet connections |  | 100 | 7 | 0 | 1 | 150
| D/F pipes - 2m. Long | 100 | 6 | #N/A |  | #N/A |  |  |  | Outlet connections |  | 100 | 6 | 0 | 1 | 150
| D/F pipes - 0.90m. Long | 100 | 0 | #N/A |  | #N/A |  |  |  | Scour connections |  | 80 | 6 | 0 | 1 | 80
| D/F pipes - 0.60m. Long | 100 | 1 | #N/A |  | #N/A |  |  |  | Overflow connections |  | 100 | 7 | 0 | 1 | 150
| Bell mouths | 100 | 1 | #N/A |  | #N/A
| Duck foot bends | 100 | 1 | #N/A |  | #N/A | [5 empty] | LPM | Size
[12 empty] | 50 | 80
3 | Scour connections | [10 empty] | 190 | 100 |  | 10 | 80
| D/F pipes - 2m. Long | 80 | 6 | #N/A |  | #N/A | [5 empty] | 300 | 125 |  | 120 | 100
| D/F pipes - 0.90m. Long | 80 | 1 | #N/A |  | #N/A | [5 empty] | 450 | 150 |  | 200 | 150
| D/F pipes - 0.60m. Long | 80 | 3 | #N/A |  | #N/A | [5 empty] | 650 | 200 |  | 300 | 200
| Bell mouths | 80 | 1 | #N/A |  | #N/A | [5 empty] | 1100 | 250 |  | 450 | 250
| Duck foot bends | 80 | 2 | #N/A |  | #N/A | [5 empty] | 1750 | 300
| Semicircular bend | 80 | 1 | #N/A |  | #N/A | [5 empty] | 2500 | 350
[12 empty] | 3500 | 400
4 | Overflow connections | [10 empty] | 4500 | 450
| D/F pipes - 2m. Long | 100 | 7 | #N/A |  | #N/A | [5 empty] | 5700 | 500
| D/F pipes - 0.90m. Long | 100 | 0 | #N/A |  | #N/A | [5 empty] | 7000 | 600
| D/F pipes - 0.60m. Long | 100 | 1 | #N/A |  | #N/A | [5 empty] | 10100 | 700
| Bell mouths | 100 | 1 | #N/A |  | #N/A | [5 empty] | 13700 | 800
| 90 D/F bends | 100 | 0 | 1250.28 |  | 0
| Tail pieces | 100 | 0 | 1429.73 |  | 0
| Duck foot bends | 100 | 1 | #N/A |  | #N/A
5 | Sluice Valves
| Sluice valve for Inlet | 100 | 1 | 13742 | Each | 13742
| Sluice valve for Outlet | 100 | 1 | 13742 | Each | 13742
| Sluice valve for Scour | 80 | 1 | 10418 | Each | 10418 |  | #N/A
| Provision for CED for CI specials |  |  |  |  | #N/A
|  |  | Total |  |  | #N/A
| Asst. Engineer |  |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  |  | RWS&S Circle Nalgonda

## sluice-PVC (hidden)
Data Sheet for Fixing Butter fly valves on PVC Mains
| PN - 16 | [12 empty] | #REF!
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 125mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x 1.05m | 0.90x0.75x1.05m | 0.90x0.75x 1.05m | 0.90x0.90x 1.40m | 0.90x0.90x1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m
A) MATERIALS
1 | DI D/F Gate valves ( soft Seated ) valves conforming to IS 3896-oart 2-1985 wedge fully rubber lined with EPDM food grade quality and the valve should be of vacuum tight and 100% leak proof with face to face dimensions. All the valves should be with Electrostatic powder caoting both insisde and outside pockets body passages.Drilled as per IS: 1538 | 9922 | 9922 | 9922 | 13088 | 11696 | 20607 | 20607 | 20607 | 34244 | 34244 | 47429 | 47429 | 71682
| Cost of Dismantling Joint (up to 300 mm dia CI and above 300 mm dia MS | 5042 | 5042 | 5042 | 6616 | 6616 | 9332 | 9332 | 9332 | 13234 | 13234 | 15754 | 15754 | 25208
2 | Transportation charges(5%) | 748.2 | 748.2 | 748.2 | 985.2 | 915.6 | 1496.95 | 1496.95 | 1496.95 | 2373.9 | 2373.9 | 3159.15 | 3159.15 | 4844.5
3 | Cost of 0.6m DI D/F pipes | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Cost of MTA's | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Cost of M S threaded flanges two nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Jointing materials such as bolts nuts and rubber vouchers including labour charges for main line - 5 jobs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | Jointing materials such as bolts nuts and rubber vouchers for Sluice valve fixing | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | Labour charges for lowering CI pipes (2 jobs) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | Lowering of valve and keeping in postion | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | Cost of RCC valve chamber | 12570 | 12570 | 12570 | 17025 | 17025 | 17025 | 17025 | 17025 | 17025 | 17025 | 25466 | 25466 | 25466
12 | Add: contractors profit 13.615% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Grand total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PN - 1.60
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 125mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 1.05x1.20x1.70m | 1.05x1.20x1.70m | 1.05x1.20x1.70m
A) MATERIALS
1 | Cost of butterfly valve PN 1.6 | 3135 | 3135 | 3135 | 4389 | 5472 | 6612 | 6612 | 6612 | 11400 | 11400 | 18050 | 18050 | 23750
2 | Conveyance of valves and accessories including loading at factory and unloading, stacking at site of work. | 313.5 | 313.5 | 313.5 | 438.9 | 547.2 | 661.2 | 661.2 | 661.2 | 1140 | 1140 | 1805 | 1805 | 2375
3 | Cost of 0.6m D/F pipes | 1282.12 | 1282.12 | 1282.12 | 1572.06 | 2025.6 | 2550.94 | 2550.94 | 2550.94 | 3634.9 | 3634.9 | 4859.82 | 4859.82 | 6201.8
4 | Cost of MTA's | 50 | 70 | 90 | 100 | 142 | 165 | 188 | 220 | 260 | 280 | 340 | 380 | 420
5 | Cost of Dismantling Joint | 1082 | 1082 | 1082 | 1332 | 1720 | 2130 | 2130 | 2130 | 3532 | 3532 | 4995 | 4995 | 6348
6 | Cost of M S threaded flanges two nos | 360 | 360 | 360 | 440 | 560 | 560 | 640 | 720 | 780 | 825 | 840 | 860 | 860
7 | Jointing materials such as bolts nuts and rubber vouchers for main line jointing 5nos | 367.9 | 367.9 | 367.9 | 660.9 | 691.25 | 912.35 | 912.35 | 912.35 | 193.94 | 193.94 | 1419.1 | 1419.1 | 1505.2
| Part A - Total | 6591 | 6611 | 6631 | 8933 | 11158 | 13591 | 13694 | 13806 | 20941 | 21006 | 32309 | 32369 | 41460
B) LABOUR COMPONENT
8 | Labour charges for 5 nos flanged joints | 275.5 | 275.5 | 275.5 | 293.5 | 424 | 441.5 | 441.5 | 441.5 | 582.5 | 582.5 | 720 | 720 | 862.5
9 | Lowering of valve and keeping in postion | 23.2 | 23.2 | 23.2 | 30.6 | 40.1 | 47.4 | 47.4 | 47.4 | 87.7 | 87.7 | 118.6 | 118.6 | 179.6
10 | Lowering Charges of D/F pipes | 21.12 | 21.12 | 21.12 | 21.12 | 21.12 | 22.08 | 22.08 | 22.56 | 24.72 | 26.4 | 28.08 | 28.08 | 35.88
11 | Cost of RCC valve chamber | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
12 | Add: LA & LI on labour comp at 13% | 41.5766 | 41.5766 | 41.5766 | 44.8786 | 63.0786 | 66.4274 | 66.4274 | 66.4898 | 90.3396 | 90.558 | 112.6684 | 112.6684 | 140.1374
| Part B - Total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Grand total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## CI (hidden)
| Requirement of CI Specials |  |  | SSR 2016 - 17 | [5 empty] | Taxes | 1
| Side wall depth | [5 empty] | : | 1.9 | m |  | Rates of various materials
| Staging of the OHSR | [5 empty] | : | 9 | m | Size | 2m d/f | .9m d/f | .6 d/f | bellmouth | 90 bend | tpiece | DuFbend | semicir | sluice valve
| Discharge through inlet pipe |  |  | #N/A |  | 42 | : | 42 | LPM | 80 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10418
| Diameter of pipe |  |  |  |  | 80 |  | 80 | mm | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13742
[10 empty] | 125 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19460
Sub Estimate
Requirement of CI Specials for the OHSR with 9 mtr staging | [9 empty] | 150 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21637
S. No. | Description | Dia. Req | No's | Rate | Per | Amount |  |  |  | 250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49800
1 | Inlet connections | [8 empty] | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 75266
| D/F pipes - 2m. Long | 80 | 5 | #N/A |  | #N/A |  |  |  | 350 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 227882
| D/F pipes - 0.90m. Long | 80 | 1 | #N/A |  | #N/A |  |  |  | 400 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 239013
| D/F pipes - 0.60m. Long | 80 | 1 | #N/A |  | #N/A |  |  |  | 450 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 411203
| 90 D/F bends | 80 | 1 | #N/A |  | #N/A |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 436671
| Tail pieces | 80 | 1 | #N/A |  | #N/A |  |  |  | 600 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 562308
| Duck foot bends | 80 | 1 | #N/A |  | #N/A
[12 empty] | Size | 2m | .9m | .6m
2 | Outlet connections | [8 empty] | Inlet connections |  | 80 | 5 | 1 | 1 | 150
| D/F pipes - 2m. Long | 80 | 4 | #N/A |  | #N/A |  |  |  | Outlet connections |  | 80 | 4 | 1 | 1 | 150
| D/F pipes - 0.90m. Long | 80 | 1 | #N/A |  | #N/A |  |  |  | Scour connections |  | 80 | 4 | 1 | 1 | 80
| D/F pipes - 0.60m. Long | 80 | 1 | #N/A |  | #N/A |  |  |  | Overflow connections |  | 80 | 5 | 1 | 1 | 150
| Bell mouths | 80 | 1 | #N/A |  | #N/A
| Duck foot bends | 80 | 1 | #N/A |  | #N/A | [5 empty] | LPM | Size
[12 empty] | 50 | 80
3 | Scour connections | [10 empty] | 190 | 100 |  | 10 | 80
| D/F pipes - 2m. Long | 80 | 4 | #N/A |  | #N/A | [5 empty] | 300 | 125 |  | 120 | 100
| D/F pipes - 0.90m. Long | 80 | 2 | #N/A |  | #N/A | [5 empty] | 450 | 150 |  | 200 | 150
| D/F pipes - 0.60m. Long | 80 | 3 | #N/A |  | #N/A | [5 empty] | 650 | 200 |  | 300 | 200
| Bell mouths | 80 | 1 | #N/A |  | #N/A | [5 empty] | 1100 | 250 |  | 450 | 250
| Duck foot bends | 80 | 2 | #N/A |  | #N/A | [5 empty] | 1750 | 300
| Semicircular bend | 80 | 1 | #N/A |  | #N/A | [5 empty] | 2500 | 350
[12 empty] | 3500 | 400
4 | Overflow connections | [10 empty] | 4500 | 450
| D/F pipes - 2m. Long | 80 | 5 | #N/A |  | #N/A | [5 empty] | 5700 | 500
| D/F pipes - 0.90m. Long | 80 | 1 | #N/A |  | #N/A | [5 empty] | 7000 | 600
| D/F pipes - 0.60m. Long | 80 | 1 | #N/A |  | #N/A | [5 empty] | 10100 | 700
| Bell mouths | 80 | 1 | #N/A |  | #N/A | [5 empty] | 13700 | 800
| 90 D/F bends | 80 | 1 | #N/A |  | #N/A
| Tail pieces | 80 | 1 | #N/A |  | #N/A
| Duck foot bends | 80 | 1 | #N/A |  | #N/A
5 | Sluice Valves
| Sluice valve for Inlet | 80 | 1 | 10418 | Each | 10418
| Sluice valve for Outlet | 80 | 1 | 10418 | Each | 10418
| Sluice valve for Scour | 80 | 1 | 10418 | Each | 10418 |  | #N/A
| Provision for CED for CI specials |  |  |  |  | #N/A
|  |  | Total |  |  | #N/A
| Asst. Engineer |  |  |  | Dy. Exe Engineer
| RWS & S Thirumalagiri |  |  |  | RWS Subdivision Thungathurthy
| Executive Engineer |  |  | Superintending Engineer
| RWS&S Div-I Nalgonda |  |  | RWS&S Circle Nalgonda

## OHSR 16-17 (hidden)
|  | STANDARD SCHEDULE OF RATES FOR THE YEAR | 2016-17
SNo | Item No | Description of Item | Rate | Per
Material rates
|  | Cement | 5600 | 1 M.T.
|  | Steel | 37000 | 1 M.T.
Seignorage Charges
|  | Seignorage charges for metal | 50 | 1 Cum
|  | Seignorage charges for sand | 40 | 1 Cum
[5 empty] | Amnt |  |  | Amnt
| OHSR rates | (capacity in litres | Rate per 1 litre |  | 16-17 | 15-16 | diff | 16-17 | 15-16 | diff
|  | 10000 | 72.13 |  | 721300 | 603500 | 117800 | 72.13 | 60.35 | 11.78
|  | 15000 | 45.64 |  | 684600 | 622650 | 61950 | 45.64 | 41.51 | 4.13
|  | 20000 | 42.9 |  | 858000 | 815800 | 42200 | 42.9 | 40.79 | 2.11
|  | 40000 | 34.53 |  | 1381200 | 1444400 | -63200 | 34.53 | 36.11 | -1.58
|  | 60000 | 23.58 |  | 1414800 | 1644000 | -229200 | 23.58 | 27.4 | -3.82
|  | 100000 | 19.34 |  | 1934000 | 2529000 | -595000 | 19.34 | 25.29 | -5.95
|  | 200000 | 16.94 |  | 3388000 | 4428000 | -1040000 | 16.94 | 22.14 | -5.2
|  | 300000 | 15.89 |  | 4767000 | 6231000 | -1464000 | 15.89 | 20.77 | -4.88
|  | 400000 | 14.02 |  | 5608000 | 7328000 | -1720000 | 14.02 | 18.32 | -4.3
|  | 450000 | 12.14 |  | 5463000 | 7146000 | -1683000 | 12.14 | 15.88 | -3.74
|  | cement rate worked out for OHSR | 5500
|  | Steel rate worked out for OHSR | 33000
PVC PIPES COST As on Dt : 01-12-2013.
|  | 180 MM DIA / 6 KG | 601.69
|  | 110 MM DIA / 6 KG | 220.62
|  | 90 MM DIA / 6 KG | 152.19
|  | 75 MM DIA / 6 KG | 105
|  | 63 MM DIA / 6 KG | 76.68
|  | 110 MM DIA / 4 KG | 153.96
|  | 90 MM DIA / 4 KG | 106.18
|  | 75 MM DIA / 4 KG | 77.87
|  | 63 MM DIA / 4 KG | 53.09
LAYING & JOINTING OF PVC PIPES
|  | 63 MM DIA PVC PIPES | 53.9
|  | 75 MM DIA PVC PIPES | 54.75
|  | 90 MM DIA PVC PIPES | 79.8
|  | 110 MM DIA PVC PIPES | 81.2
140 MM DIA PVC PIPES
BORE WELL
|  | Drilling of 163 mm dia borewell | 285
|  | Casing pipe of 180 mm dia | 601.69
S/F OF PUMPSETS
|  | 5 HP / 8 STAGES SUBMERSIBLE PUMPSET | 65000
|  | 7.5 HP MONO BLOCK PUMPSET | 90000
Rates of CI pipes and specials
| 80 | 80mm dia D/F pipes - 2m Long | 1562.75
|  | 80mm dia D/F pipes - 0.90m Long | 838.57
|  | 80mm dia D/F pipes - 0.60m Long | 641.06
|  | 80mm dia Tail pieces | 399
|  | 80mm dia Semicircular bend | 845.88
|  | 80mm dia Duck foot bends | 698.25
|  | 80mm dia Bell mouths | 232.75
|  | 80mm dia 90 D/F bends | 432.25
|  | 80mm dia CI D/F sluice valve PN-1.0 | 4255
|  | 80mm dia wafer type butterfly valve PN-1.0 | 2265
| 100 | 100mm dia D/F pipes - 2m Long | 1968.4
|  | 100mm dia D/F pipes - 0.90m Long | 1039.4
|  | 100mm dia D/F pipes - 0.60m Long | 786.03
|  | 100mm dia Tail pieces | 449.32
|  | 100mm dia Semicircular bend | 1175.72
|  | 100mm dia Duck foot bends | 864.5
|  | 100mm dia Bell mouths | 299.25
|  | 100mm dia 90 D/F bends | 565.25
|  | 100mm dia CI D/F sluice valve PN-1.0 | 5673
|  | 100mm dia wafer type butterfly valve PN-1.0 | 3088
| 125 | 125mm dia D/F pipes - 2m Long | 2553.6
|  | 125mm dia D/F pipes - 0.90m Long | 1342.96
|  | 125mm dia D/F pipes - 0.60m Long | 1012.8
|  | 125mm dia Tail pieces | 631.75
|  | 125mm dia Semicircular bend | 1689.1
|  | 125mm dia Duck foot bends | 1197
|  | 125mm dia Bell mouths | 399
|  | 125mm dia 90 D/F bends | 764.75
|  | 125mm dia CI D/F sluice valve PN-1.0 | 7090
|  | 125mm dia wafer type butterfly valve PN-1.0 | 4245
| 150 | 150mm dia D/F pipes - 2m Long | 3211.95
|  | 150mm dia D/F pipes - 0.90m Long | 1690.43
|  | 150mm dia D/F pipes - 0.60m Long | 1817.45
|  | 150mm dia Tail pieces | 764.75
|  | 150mm dia Semicircular bend | 2364.74
|  | 150mm dia Duck foot bends | 1561.85
|  | 150mm dia Bell mouths | 498.75
|  | 150mm dia 90 D/F bends | 1029.85
|  | 150mm dia CI D/F sluice valve PN-1.0 | 8509
|  | 150mm dia wafer type butterfly valve PN-1.0 | 4762
| 200 | 200mm dia D/F pipes - 2m Long | 4615.1
|  | 200mm dia D/F pipes - 0.90m Long | 2416.94
|  | 200mm dia D/F pipes - 0.60m Long | 1817.45
|  | 200mm dia Tail pieces | 1295.85
|  | 200mm dia Semicircular bend | 3885.27
|  | 200mm dia Duck foot bends | 2460.5
|  | 200mm dia Bell mouths | 764.75
|  | 200mm dia 90 D/F bends | 1629.25
|  | 200mm dia CI D/F sluice valve PN-1.0 | 14914
|  | 200mm dia wafer type butterfly valve PN-1.0 | 13124

## ew OG 25% (2) (hidden)
Data based on 2017-18 Common SSR
[5 empty] | Muncipal /Agency |  |  | 25%
| Earthwork excavation in all soils upto SDR using 1/3 machinery and 2/3rd manual labour | [11 empty] | Common SSR | 2017-18
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | 102.8533 | - | 102.8533 | Cost of sand for filling |  | - |  | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead |  | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 |  | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 0 | - | 0 | Filling charges |  | - |  | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | 220.22 |  | 220.22 | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  |  | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 1/3rd machinery & 2/3rd manual |  | 181.1 | /cum |  |  | Total: | 0 |  |  |  |  | Total: | 220.22 |  |  | 313.0702
|  | Extra Allowance for trench cutting |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | 220.22
| PVC pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033 | 0 | 0
|  | Total | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033
PVC pipes - Earth work-Part-B
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 235.43 | 235.43
2 | Extra allowance at 75% |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | 10.58 | 12.6 | 15.12 | 18.48 | 21 | 23.52 | 26.88 | 30.24 | 33.6 | 37.8 | 42 | 47.04 | 52.92
6 | Cost of specials (1.20%) with same pressure gauge |  | 0.972 | 1.344 | 1.932 | 2.796 | 3.576 | 4.596 | 5.952 | 7.668 | 9.336 | 12.54 | 15.348 | 19.404 | 24.396
6 | Add CF 13.615% |  | 29.327 | 29.6527 | 30.0758 | 30.6509 | 31.1002 | 31.5822 | 39.3612 | 40.0523 | 40.7369 | 49.6743 | 50.6285 | 51.8669 | 53.3471
|  |  | 244.73 | 247.45 | 250.98 | 255.78 | 259.53 | 263.55 | 328.46 | 334.23 | 339.94 | 414.52 | 422.49 | 432.82 | 445.17
|  | 25% Muncipal/Agency allowance for Earth work | 19.6317 | 20.1367 | 20.7667 | 21.6067 | 22.2367 | 22.8667 | 28.0747 | 28.9147 | 29.7547 | 35.658 | 36.708 | 37.968 | 39.438 | 16.9867 | 16.9867 | 16.9867 | 16.9867
|  | Total: | 264.3617 | 267.5867 | 271.7467 | 277.3867 | 281.7667 | 286.4167 | 356.5347 | 363.1447 | 369.6947 | 450.178 | 459.198 | 470.788 | 484.608
0
| HDPE pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435 | 0 | 0
|  | Total; | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435
HDPE pipes - Earth work - Part-B
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 253.54 | 253.54 | 253.54
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 77.08 | 77.08 | 77.08
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing |  | 39 | 43 | 48 | 59 | 70 | 74 | 80 | 88 | 96 | 106 | 112 | 124 | 192 | 204 | 227 | 252
| Cost of specials (0.50%) with same pressure gauge |  | 0.49 | 0.69 | 0.985 | 1.48 | 1.89 | 2.37 | 3.105 | 3.9 | 4.82 | 6.225 | 7.66 | 9.605 | 12.175
5 | Add CF 13.615% |  | 33.1307 | 33.7026 | 34.4235 | 35.9885 | 37.542 | 38.152 | 46.2059 | 47.4033 | 48.6178 | 58.1 | 59.1122 | 61.0109 | 70.619 | 70.8198 | 76.5698 | 82.8198
|  |  | 276.47 | 281.24 | 287.26 | 300.32 | 313.28 | 318.37 | 385.58 | 395.57 | 405.71 | 484.83 | 493.28 | 509.13 | 589.3 | 605.44 | 634.19 | 665.44
|  | 25% | 26.7367 | 27.7367 | 28.9867 | 31.7367 | 34.4867 | 35.4867 | 41.3547 | 43.3547 | 45.3547 | 52.708 | 54.208 | 57.208 | 74.208
|  | Total: | 303.2067 | 308.9767 | 316.2467 | 332.0567 | 347.7667 | 353.8567 | 426.9347 | 438.9247 | 451.0647 | 537.538 | 547.488 | 566.338 | 663.508 | 605.44 | 634.19 | 665.44 | 0
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 608.496 | 941.72
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 286.29
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | 560.62 | 596.62 | 698.64 | 829.75 | 960.6 | 1090.18 | 1214.47 | 1377.48 | 1884.01
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | 102.1923 | 115.6923 | 132.1923 | 144.6923 | 181.2989 | 220.6874 | 256.4429 | 291.5654 | 340.555 | 370.555 | 0 | 0
|  | Total | 738.81 | 806.31 | 888.81 | 951.31 | 1192.93 | 1435.44 | 1663.05 | 1890.74 | 2191.03 | 2397.06 | 2375.58 | 4820.73
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | 266.6697 | 289.76 | 313.7557 | 338.657 | 391.176 | 447.317 | 507.08 | 570.465 | 637.472 | #VALUE!
2 | Extra allowance |  | 81.07 | 88.09 | 95.38 | 102.95 | 118.92 | 135.99 | 154.15 | 173.42 | 193.79 | 0
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 507.08 | 507.08 | 570.465 | 570.465 | 666.448
2 | Extra allowance |  | 59.46 | 59.46 | 59.46 | 59.46 | 64.41 | 64.41 | 64.41 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31 | 128.83 | 154.15 | 154.15 | 173.42 | 173.42 | 202.6
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | 255.048 | 255.048 | 255.048 | 255.048 | 276.297 | 276.297 | 276.297 | 330.62 | 330.62 | 357.7164 | 415.636 | 481.754 | 552.604 | 661.23 | 661.23 | 743.885 | 743.885 | 869.048
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | 28.5698 | 32.8198 | 34.0698 | 36.8198 | 43.7215 | 48.2215 | 54.4715 | 81.6923 | 109.6923 | 127.9423 | 162.2989 | 177.1874 | 198.9429 | 224.8847 | 233.8847 | 252.5577 | 270.3077 | 286.2841
|  | Total | 318.6178 | 339.8678 | 346.1178 | 359.8678 | 409.0185 | 431.5185 | 462.7685 | 636.3123 | 776.3123 | 894.6587 | 1097.9349 | 1217.9414 | 1375.5469 | 1580.1147 | 1625.1147 | 1775.4427 | 1864.1927 | 2030.3321
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444
| 2 | Extra allowance | 59.46 | 59.46 | 21.66 | 59.46 | 64.41 | 64.41 | 21.66 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31
| 3 | Sand cushion cost | 0 | 0 | 0 | 0 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352 | 860.225 | 941.72 | 1026.837 | 1115.576 | 1207.937 | 1303.92 | 1403.525 | 1506.752
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | 102.1923 | 115.6923 | 137.9423 | 157.6923 | 176.0489 | 205.6874 | 234.6929 | 268.8154 | 303.055 | 326.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 738.81 | 806.31 | 917.56 | 1016.31 | 1166.68 | 1360.44 | 1554.3 | 1776.99 | 2003.53 | 2178.31 | 2124.58 | 4504.73 | 4677.61 | 4904.1 | 5163.22 | 5396.96 | 5729.32 | 5954.3 | 6259.91 | 6523.13
Note on J7: to be changed based on the corresponding lead from master copy

## ew OG 20% (hidden)
Data based on 2017-18 Common SSR
[5 empty] | District Head Quertors |  |  | 20%
| Earthwork excavation in all soils upto SDR using 1/3 machinery and 2/3rd manual labour | [11 empty] | Common SSR | 2017-18
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | 102.8533 | - | 102.8533 | Cost of sand for filling |  | - |  | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead |  | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 |  | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 0 | - | 0 | Filling charges |  | - |  | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | 220.22 |  | 220.22 | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  |  | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 1/3rd machinery & 2/3rd manual |  | 181.1 | /cum |  |  | Total: | 0 |  |  |  |  | Total: | 220.22 |  |  | 313.0702
|  | Extra Allowance for trench cutting |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | 220.22
PVC pipes -Materail component-Part-A
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033 | 0 | 0
|  | Total | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033
PVC pipes - Earth work-Part-B
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 235.43 | 235.43
2 | Extra allowance at 75% |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | 10.58 | 12.6 | 15.12 | 18.48 | 21 | 23.52 | 26.88 | 30.24 | 33.6 | 37.8 | 42 | 47.04 | 52.92
6 | Cost of specials (1.20%) with same pressure gauge |  | 0.972 | 1.344 | 1.932 | 2.796 | 3.576 | 4.596 | 5.952 | 7.668 | 9.336 | 12.54 | 15.348 | 19.404 | 24.396
6 | Add CF 13.615% |  | 29.327 | 29.6527 | 30.0758 | 30.6509 | 31.1002 | 31.5822 | 39.3612 | 40.0523 | 40.7369 | 49.6743 | 50.6285 | 51.8669 | 53.3471
|  |  | 244.73 | 247.45 | 250.98 | 255.78 | 259.53 | 263.55 | 328.46 | 334.23 | 339.94 | 414.52 | 422.49 | 432.82 | 445.17
|  | 20% Dist. Head Qrt allowance for Earth work | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 25.8391 | 25.8391 | 25.8391 | 31.7117 | 31.7117 | 31.7117 | 31.7117
|  | Total: | 265.2839 | 268.0039 | 271.5339 | 276.3339 | 280.0839 | 284.1039 | 354.2991 | 360.0691 | 365.7791 | 446.2317 | 454.2017 | 464.5317 | 476.8817
HDPE pipes -Materail component-Part-A
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435 | 0 | 0
|  | Total; | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435
HDPE pipes - Earth work - Part-B
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 253.54 | 253.54 | 253.54
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 77.08 | 77.08 | 77.08
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing |  | 39 | 43 | 48 | 59 | 70 | 74 | 80 | 88 | 96 | 106 | 112 | 124 | 192 | 204 | 227 | 252
| Cost of specials (0.50%) with same pressure gauge |  | 0.49 | 0.69 | 0.985 | 1.48 | 1.89 | 2.37 | 3.105 | 3.9 | 4.82 | 6.225 | 7.66 | 9.605 | 12.175
5 | Add CF 13.615% |  | 33.1307 | 33.7026 | 34.4235 | 35.9885 | 37.542 | 38.152 | 46.2059 | 47.4033 | 48.6178 | 58.1 | 59.1122 | 61.0109 | 70.619 | 56.6558 | 61.2558 | 66.2558
|  |  | 276.47 | 281.24 | 287.26 | 300.32 | 313.28 | 318.37 | 385.58 | 395.57 | 405.71 | 484.83 | 493.28 | 509.13 | 589.3 | 591.28 | 618.88 | 648.88
|  | 20% Dist. Head Qrt allowance for Earth work | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 20.5539 | 25.8391 | 25.8391 | 25.8391 | 31.7117 | 31.7117 | 31.7117 | 31.7117
|  | Total: | 297.0239 | 301.7939 | 307.8139 | 320.8739 | 333.8339 | 338.9239 | 411.4191 | 421.4091 | 431.5491 | 516.5417 | 524.9917 | 540.8417 | 621.0117 | 591.28 | 618.88 | 648.88 | 0
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 608.496 | 941.72
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 286.29
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | 560.62 | 596.62 | 698.64 | 829.75 | 960.6 | 1090.18 | 1214.47 | 1377.48 | 1884.01
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | 81.7539 | 92.5539 | 105.7539 | 115.7539 | 145.0391 | 176.5499 | 205.1543 | 233.2523 | 272.444 | 296.444 | 0 | 0
|  | Total | 718.37 | 783.17 | 862.37 | 922.37 | 1156.68 | 1391.3 | 1611.76 | 1832.43 | 2122.91 | 2322.94 | 2375.58 | 4820.73
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | 266.6697 | 289.76 | 313.7557 | 338.657 | 391.176 | 447.317 | 507.08 | 570.465 | 637.472 | #VALUE!
2 | Extra allowance |  | 81.07 | 88.09 | 95.38 | 102.95 | 118.92 | 135.99 | 154.15 | 173.42 | 193.79 | 0
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 507.08 | 507.08 | 570.465 | 570.465 | 666.448
2 | Extra allowance |  | 59.46 | 59.46 | 59.46 | 59.46 | 64.41 | 64.41 | 64.41 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31 | 128.83 | 154.15 | 154.15 | 173.42 | 173.42 | 202.6
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | 255.048 | 255.048 | 255.048 | 255.048 | 276.297 | 276.297 | 276.297 | 330.62 | 330.62 | 357.7164 | 415.636 | 481.754 | 552.604 | 661.23 | 661.23 | 743.885 | 743.885 | 869.048
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | 22.8558 | 26.2558 | 27.2558 | 29.4558 | 34.9772 | 38.5772 | 43.5772 | 65.3539 | 87.7539 | 102.3539 | 129.8391 | 141.7499 | 159.1543 | 179.9077 | 187.1077 | 202.0462 | 216.2462 | 229.0273
|  | Total | 312.9038 | 333.3038 | 339.3038 | 352.5038 | 400.2742 | 421.8742 | 451.8742 | 619.9739 | 754.3739 | 869.0702 | 1065.4751 | 1182.5039 | 1335.7583 | 1535.1377 | 1578.3377 | 1724.9312 | 1810.1312 | 1973.0753
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444
| 2 | Extra allowance | 59.46 | 59.46 | 21.66 | 59.46 | 64.41 | 64.41 | 21.66 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31
| 3 | Sand cushion cost | 0 | 0 | 0 | 0 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352 | 860.225 | 941.72 | 1026.837 | 1115.576 | 1207.937 | 1303.92 | 1403.525 | 1506.752
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | 81.7539 | 92.5539 | 110.3539 | 126.1539 | 140.8391 | 164.5499 | 187.7543 | 215.0523 | 242.444 | 261.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 718.37 | 783.17 | 889.97 | 984.77 | 1131.48 | 1319.3 | 1507.36 | 1723.23 | 1942.91 | 2112.94 | 2124.58 | 4504.73 | 4677.61 | 4904.1 | 5163.22 | 5396.96 | 5729.32 | 5954.3 | 6259.91 | 6523.13
Note on J7: to be changed based on the corresponding lead from master copy

## ew OG 25% (hidden)
Data based on 2017-18 Common SSR
[5 empty] | Muncipal /Agency |  |  | 25%
| Earthwork excavation in all soils upto SDR using 1/3 machinery and 2/3rd manual labour | [11 empty] | Common SSR | 2017-18
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | 102.8533 | - | 102.8533 | Cost of sand for filling |  | - |  | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead |  | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 |  | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 0 | - | 0 | Filling charges |  | - |  | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | 220.22 |  | 220.22 | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  |  | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 1/3rd machinery & 2/3rd manual |  | 181.1 | /cum |  |  | Total: | 0 |  |  |  |  | Total: | 220.22 |  |  | 313.0702
|  | Extra Allowance for trench cutting |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | 220.22
| PVC pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033 | 0 | 0
|  | Total | 81 | 112 | 161 | 233 | 298 | 383 | 496 | 639 | 778 | 1045 | 1279 | 1617 | 2033
PVC pipes - Earth work-Part-B
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 235.43 | 235.43
2 | Extra allowance at 75% |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | 10.58 | 12.6 | 15.12 | 18.48 | 21 | 23.52 | 26.88 | 30.24 | 33.6 | 37.8 | 42 | 47.04 | 52.92
6 | Cost of specials (1.20%) with same pressure gauge |  | 0.972 | 1.344 | 1.932 | 2.796 | 3.576 | 4.596 | 5.952 | 7.668 | 9.336 | 12.54 | 15.348 | 19.404 | 24.396
6 | Add CF 13.615% |  | 29.327 | 29.6527 | 30.0758 | 30.6509 | 31.1002 | 31.5822 | 39.3612 | 40.0523 | 40.7369 | 49.6743 | 50.6285 | 51.8669 | 53.3471
|  |  | 244.73 | 247.45 | 250.98 | 255.78 | 259.53 | 263.55 | 328.46 | 334.23 | 339.94 | 414.52 | 422.49 | 432.82 | 445.17
|  | 25% Muncipal/Agency allowance for Earth work | 19.6317 | 20.1367 | 20.7667 | 21.6067 | 22.2367 | 22.8667 | 28.0747 | 28.9147 | 29.7547 | 35.658 | 36.708 | 37.968 | 39.438 | 16.9867 | 16.9867 | 16.9867 | 16.9867
|  | Total: | 264.3617 | 267.5867 | 271.7467 | 277.3867 | 281.7667 | 286.4167 | 356.5347 | 363.1447 | 369.6947 | 450.178 | 459.198 | 470.788 | 484.608
0
| HDPE pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435 | 0 | 0
|  | Total; | 98 | 138 | 197 | 296 | 378 | 474 | 621 | 780 | 964 | 1245 | 1532 | 1921 | 2435
HDPE pipes - Earth work - Part-B
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 253.54 | 253.54 | 253.54
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 77.08 | 77.08 | 77.08
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing |  | 39 | 43 | 48 | 59 | 70 | 74 | 80 | 88 | 96 | 106 | 112 | 124 | 192 | 204 | 227 | 252
| Cost of specials (0.50%) with same pressure gauge |  | 0.49 | 0.69 | 0.985 | 1.48 | 1.89 | 2.37 | 3.105 | 3.9 | 4.82 | 6.225 | 7.66 | 9.605 | 12.175
5 | Add CF 13.615% |  | 33.1307 | 33.7026 | 34.4235 | 35.9885 | 37.542 | 38.152 | 46.2059 | 47.4033 | 48.6178 | 58.1 | 59.1122 | 61.0109 | 70.619 | 70.8198 | 76.5698 | 82.8198
|  |  | 276.47 | 281.24 | 287.26 | 300.32 | 313.28 | 318.37 | 385.58 | 395.57 | 405.71 | 484.83 | 493.28 | 509.13 | 589.3 | 605.44 | 634.19 | 665.44
|  | 25% | 26.7367 | 27.7367 | 28.9867 | 31.7367 | 34.4867 | 35.4867 | 41.3547 | 43.3547 | 45.3547 | 52.708 | 54.208 | 57.208 | 74.208
|  | Total: | 303.2067 | 308.9767 | 316.2467 | 332.0567 | 347.7667 | 353.8567 | 426.9347 | 438.9247 | 451.0647 | 537.538 | 547.488 | 566.338 | 663.508 | 605.44 | 634.19 | 665.44 | 0
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 608.496 | 941.72
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 286.29
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | 560.62 | 596.62 | 698.64 | 829.75 | 960.6 | 1090.18 | 1214.47 | 1377.48 | 1884.01
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | 102.1923 | 115.6923 | 132.1923 | 144.6923 | 181.2989 | 220.6874 | 256.4429 | 291.5654 | 340.555 | 370.555 | 0 | 0
|  | Total | 738.81 | 806.31 | 888.81 | 951.31 | 1192.93 | 1435.44 | 1663.05 | 1890.74 | 2191.03 | 2397.06 | 2375.58 | 4820.73
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | 266.6697 | 289.76 | 313.7557 | 338.657 | 391.176 | 447.317 | 507.08 | 570.465 | 637.472 | #VALUE!
2 | Extra allowance |  | 81.07 | 88.09 | 95.38 | 102.95 | 118.92 | 135.99 | 154.15 | 173.42 | 193.79 | 0
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 507.08 | 507.08 | 570.465 | 570.465 | 666.448
2 | Extra allowance |  | 59.46 | 59.46 | 59.46 | 59.46 | 64.41 | 64.41 | 64.41 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31 | 128.83 | 154.15 | 154.15 | 173.42 | 173.42 | 202.6
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | 255.048 | 255.048 | 255.048 | 255.048 | 276.297 | 276.297 | 276.297 | 330.62 | 330.62 | 357.7164 | 415.636 | 481.754 | 552.604 | 661.23 | 661.23 | 743.885 | 743.885 | 869.048
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | 28.5698 | 32.8198 | 34.0698 | 36.8198 | 43.7215 | 48.2215 | 54.4715 | 81.6923 | 109.6923 | 127.9423 | 162.2989 | 177.1874 | 198.9429 | 224.8847 | 233.8847 | 252.5577 | 270.3077 | 286.2841
|  | Total | 318.6178 | 339.8678 | 346.1178 | 359.8678 | 409.0185 | 431.5185 | 462.7685 | 636.3123 | 776.3123 | 894.6587 | 1097.9349 | 1217.9414 | 1375.5469 | 1580.1147 | 1625.1147 | 1775.4427 | 1864.1927 | 2030.3321
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444
| 2 | Extra allowance | 59.46 | 59.46 | 21.66 | 59.46 | 64.41 | 64.41 | 21.66 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31
| 3 | Sand cushion cost | 0 | 0 | 0 | 0 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352 | 860.225 | 941.72 | 1026.837 | 1115.576 | 1207.937 | 1303.92 | 1403.525 | 1506.752
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | 102.1923 | 115.6923 | 137.9423 | 157.6923 | 176.0489 | 205.6874 | 234.6929 | 268.8154 | 303.055 | 326.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 738.81 | 806.31 | 917.56 | 1016.31 | 1166.68 | 1360.44 | 1554.3 | 1776.99 | 2003.53 | 2178.31 | 2124.58 | 4504.73 | 4677.61 | 4904.1 | 5163.22 | 5396.96 | 5729.32 | 5954.3 | 6259.91 | 6523.13
Note on J7: to be changed based on the corresponding lead from master copy

## sluice-PVC (2) (hidden)
Data Sheet for Fixing Butter fly valves on PVC Mains
| PN - 16 | [12 empty] | #REF!
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 100mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x 1.05m | 0.90x0.75x1.05m | 0.90x0.75x 1.05m | 0.90x0.90x 1.40m | 0.90x0.90x1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m
A) MATERIALS
1 | DI D/F Gate valves ( soft Seated ) valves conforming to IS 3896-oart 2-1985 wedge fully rubber lined with EPDM food grade quality and the valve should be of vacuum tight and 100% leak proof with face to face dimensions. All the valves should be with Electrostatic powder caoting both insisde and outside pockets body passages.Drilled as per IS: 1538 | 9922 | 9922 | 9922 | 13088 | 13088 | 20607 | 20607 | 20607 | 34244 | 34244 | 47429 | 47429 | 71682
| Cost of Dismantling Joint (up to 300 mm dia CI and above 300 mm dia MS | 5042 | 5042 | 5042 | 6616 | 6616 | 9332 | 9332 | 9332 | 13234 | 13234 | 15754 | 15754 | 25208
2 | Transportation charges(5%) | 748.2 | 748.2 | 748.2 | 985.2 | 985.2 | 1496.95 | 1496.95 | 1496.95 | 2373.9 | 2373.9 | 3159.15 | 3159.15 | 4844.5
3 | Cost of 0.6m DI D/F pipes | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Cost of MTA's | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Cost of M S threaded flanges two nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Jointing materials such as bolts nuts and rubber vouchers including labour charges for main line - 5 jobs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | Jointing materials such as bolts nuts and rubber vouchers for Sluice valve fixing | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | Labour charges for lowering CI pipes (2 jobs) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | Lowering of valve and keeping in postion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Cost of RCC valve chamber | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Add: contractors profit 13.615% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Grand total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PN - 1.60
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 125mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 1.05x1.20x1.70m | 1.05x1.20x1.70m | 1.05x1.20x1.70m
A) MATERIALS
1 | Cost of butterfly valve PN 1.6 | 3135 | 3135 | 3135 | 4389 | 5472 | 6612 | 6612 | 6612 | 11400 | 11400 | 18050 | 18050 | 23750
2 | Conveyance of valves and accessories including loading at factory and unloading, stacking at site of work. | 313.5 | 313.5 | 313.5 | 438.9 | 547.2 | 661.2 | 661.2 | 661.2 | 1140 | 1140 | 1805 | 1805 | 2375
3 | Cost of 0.6m D/F pipes | 1282.12 | 1282.12 | 1282.12 | 1572.06 | 2025.6 | 2550.94 | 2550.94 | 2550.94 | 3634.9 | 3634.9 | 4859.82 | 4859.82 | 6201.8
4 | Cost of MTA's | 50 | 70 | 90 | 100 | 142 | 165 | 188 | 220 | 260 | 280 | 340 | 380 | 420
5 | Cost of Dismantling Joint | 1082 | 1082 | 1082 | 1332 | 1720 | 2130 | 2130 | 2130 | 3532 | 3532 | 4995 | 4995 | 6348
6 | Cost of M S threaded flanges two nos | 360 | 360 | 360 | 440 | 560 | 560 | 640 | 720 | 780 | 825 | 840 | 860 | 860
7 | Jointing materials such as bolts nuts and rubber vouchers for main line jointing 5nos | 367.9 | 367.9 | 367.9 | 660.9 | 691.25 | 912.35 | 912.35 | 912.35 | 193.94 | 193.94 | 1419.1 | 1419.1 | 1505.2
| Part A - Total | 6591 | 6611 | 6631 | 8933 | 11158 | 13591 | 13694 | 13806 | 20941 | 21006 | 32309 | 32369 | 41460
B) LABOUR COMPONENT
8 | Labour charges for 5 nos flanged joints | 275.5 | 275.5 | 275.5 | 293.5 | 424 | 441.5 | 441.5 | 441.5 | 582.5 | 582.5 | 720 | 720 | 862.5
9 | Lowering of valve and keeping in postion | 23.2 | 23.2 | 23.2 | 30.6 | 40.1 | 47.4 | 47.4 | 47.4 | 87.7 | 87.7 | 118.6 | 118.6 | 179.6
10 | Lowering Charges of D/F pipes | 21.12 | 21.12 | 21.12 | 21.12 | 21.12 | 22.08 | 22.08 | 22.56 | 24.72 | 26.4 | 28.08 | 28.08 | 35.88
11 | Cost of RCC valve chamber | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
12 | Add: LA & LI on labour comp at 13% | 41.5766 | 41.5766 | 41.5766 | 44.8786 | 63.0786 | 66.4274 | 66.4274 | 66.4898 | 90.3396 | 90.558 | 112.6684 | 112.6684 | 140.1374
| Part B - Total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Grand total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PART-A

## sluice-HDPE (hidden)
Data Sheet for Fixing Sluice valves on HDPE Mains
| PN-16 | [12 empty] | #REF!
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 125mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x 1.05m | 0.90x0.75x1.05m | 0.90x0.75x 1.05m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 0.90x0.90x 1.40m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m | 1.05x1.20x 1.70m
1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Cost of Dismantling Joint (up to 300 mm dia CI and above 300 mm dia MS | 5042 | 5042 | 5042 | 6616 | 6616 | 9332 | 9332 | 9332 | 13234 | 13234 | 15754 | 15754 | 25208
2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Cost of 0.6m DI D/F pipes 2nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Cost of HDPE Tial pieces 2 nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Cost of MS flanges 2nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Jointing materials such as bolts nuts and rubber vouchers including material cost for main line - 2nos | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | Jointing materials such as bolts nuts and rubber vouchers for Sluice valve fixing | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | Labour charges for lowering DI pipes (2 jobs) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | Lowering of valve and keeping in postion | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | Cost of RCC valve chamber | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Add: contractors profit 13.615% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Grand total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PN-1.6
SL No. | Discription of Item/ Dia of valve | 80mm dia |  |  | 100mm dia | 125mm dia | 150mm dia |  |  | 200mm dia |  | 250mm dia |  | 300mm dia
| Dia of Pipeline | 63mm line | 75mm line | 90mm line | 110mm line | 125mm line | 140mm line | 160mm line | 180mm line | 200mm line | 225mm line | 250mm line | 280mm line | 315mm line
| Size of Chamber | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.75x1.05m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 0.90x0.90x1.40m | 1.05x1.20x1.70m | 1.05x1.20x1.70m | 1.05x1.20x1.70m
A) MATERIALS
1 | Cost of butterfly valve with PN 1.0 | 3135 | 3135 | 3135 | 4389 | 5472 | 6612 | 6612 | 6612 | 11400 | 11400 | 18050 | 18050 | 23750
2 | Transportation charges (10% of basic cost) | 313.5 | 313.5 | 313.5 | 438.9 | 547.2 | 661.2 | 661.2 | 661.2 | 1140 | 1140 | 1805 | 1805 | 2375
3 | Cost of Dismantling Joint | 1082 | 1082 | 1082 | 1332 | 1720 | 2130 | 2130 | 2130 | 3532 | 3532 | 4995 | 4995 | 6348
4 | Cost of 0.6m D/F pipes 2nos | 1282.12 | 1282.12 | 1282.12 | 1572.06 | 2025.6 | 2550.94 | 2550.94 | 2550.94 | 3634.9 | 3634.9 | 4859.82 | 4859.82 | 6201.8
5 | Cost of HDPE Tial pieces 2 nos | 96 | 112 | 128 | 164 | 224 | 284 | 310 | 390 | 484 | 558 | 656 | 672 | 684
6 | Cost of MS flanges 2nos | 296 | 296 | 296 | 360 | 484 | 564 | 564 | 764 | 764 | 764 | 922 | 940 | 964
7 | Jointing materials such as bolts nuts and rubber vouchers for main line jointing 5nos | 367.9 | 367.9 | 367.9 | 660.9 | 691.25 | 912.35 | 912.35 | 912.35 | 193.94 | 193.94 | 1419.1 | 1419.1 | 1505.2
| Part A - Total | 6573 | 6589 | 6605 | 8917 | 11164 | 13714 | 13740 | 14020 | 21149 | 21223 | 32707 | 32741 | 41828
B) LABOUR CHARGES
8 | Labour charges for 5 nos flanged joints | 275.5 | 275.5 | 275.5 | 293.5 | 424 | 441.5 | 441.5 | 441.5 | 582.5 | 582.5 | 720 | 720 | 862.5
9 | Lwering of valve and keeping in postion | 23.2 | 23.2 | 23.2 | 30.6 | 40.1 | 47.4 | 47.4 | 47.4 | 87.7 | 87.7 | 118.6 | 118.6 | 179.6
10 | Lowering Charges of D/F pipes | 21.12 | 21.12 | 21.12 | 21.12 | 21.12 | 22.08 | 22.08 | 22.56 | 24.72 | 26.4 | 28.08 | 28.08 | 35.88
11 | Cost of RCC valve chamber | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
12 | Add: LA & LI on labour comp at 13% | 41.5766 | 41.5766 | 41.5766 | 44.8786 | 63.0786 | 66.4274 | 66.4274 | 66.4898 | 90.3396 | 90.558 | 112.6684 | 112.6684 | 140.1374
| Part B - Total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Grand total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Asst. Engineer |  | Dy. Executive Engineer |  |  |  | Executive Engineer |  |  |  | Superintending Engineer
| TDWSP, Palair |  | TDWSP, SD,Khammam |  |  |  | TDWSP,Divn , Khammam |  |  |  | TDWSP, Circle, Khammam.

## ew CC Portion (hidden)
Data based on 2016-17 Common SSR
[7 empty] | MA | 0%
| Earthwork excavation in all soils upto SDR using 2/3 machinery and 1/3rd manual labour | [11 empty] | Common SSR | 2015-16
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | #REF! | - | #REF! | Cost of sand for filling |  | - | 302 | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead | 796.13 | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 | 35.2066 | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 1224.7866 | - | 1224.7866 | Filling charges |  | - | 91.45 | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | #REF! |  | #REF! | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  | 0 | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 2/3rd machinery & 1/3rd manual |  | #REF! | /cum |  |  | Total: | 1224.7866 |  |  |  |  | Total: | #REF! |  |  | 313.0702
#REF!
|  | Cutting road surface including stacking of excavated materials for pipe line |  | 1878 | /cum
|  | trench work. |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | #REF!
PVC pipes - Earth work
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | CC Portion |  | 197.19 | 197.19 | 197.19 | 197.19 | 197.19 | 197.19 | 225.36 | 225.36 | 225.36 | 253.53 | 253.53 | 253.53 | 253.53 | 281.7 | 281.7
2 | Extra allowance at 75% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HDPE pipes - Earth work
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 200 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | CC Portion |  | 197.19 | 197.19 | 197.19 | 197.19 | 197.19 | 197.19 | 225.36 | 225.36 | 225.36 | 253.53 | 253.53 | 253.53 | 253.53 | 281.7 | 281.7
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing |  | 37 | 41 | 46 | 53 | 64 | 67 | 72 | 80 | 87 | 96 | 102 | 112 | 183 | 204 | 227 | 252
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0
3 | Sand cushion cost |  | 987.5316 | 1070.8754 | 1155.5334 | 1241.5055 | 1417.3925 | 1598.5363 | 1784.9369 | 1976.5943 | 2173.5086 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 104.1764 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Sand cushion cost |  | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 183.718 | 183.718 | 183.718 | 202.0898 | 220.4616 | 238.8334 | 257.2052 | 257.2052 | 275.577 | 275.577 | 293.9488
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2 | Extra allowance | #REF! | #REF! | 21.66 | #REF! | #REF! | #REF! | 21.66 | #REF! | #REF! | 104.1764 | #REF! | #REF!
| 3 | Sand cushion cost | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 165.3462 | 49.76 | 183.718 | 183.718 | 183.718 | 202.0898 | 220.4616
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Extra allowance |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on J7: to be changed based on the corresponding lead from master copy

## PVC DATA CC (hidden)
#REF! | Data based on 2016-17 Common SSR - for PVC pipes
| PVC Resin rate: | #REF! |  | exclusive of CED |  |  | Cost of specials : | 1.2 | % | Month | #REF! | #REF!
1 | PVC | 0
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Cost of specials (1.20%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Earth work, L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1 | PVC Class | 0
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Cost of specials (1.20%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Earth work, L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | PVC Class | 10
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315
A) Materials component
1 | Cost of pipe |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | `
2 | Cost of specials (1.20%) |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Earth work,L/J |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total: |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Add Contractors profit@13.615% |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PVC Specials (hidden)
SUB ESTIMATE FOR PVC SPECIALS AND ACCESSORIES
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
Sno. | Description of Work | No's |  |  | L | B | D | QTY |  | Rate | Per | Amount
1 | 63 mm dia PVC Bends | 1 | x | 6 | - | - | - | 6 | No's | 35 | / No | 210
2 | 63 mm dia PVC Couplings | 1 | x | 6 | - | - | - | 6 | No's | 20 | / No | 120
3 | 63 mm dia PVC Dummy | 1 | x | 6 | - | - | - | 6 | No's | 20 | / No | 120
4 | 63 mm dia PVC Elbow | 1 | x | 6 | - | - | - | 6 | No's | 40 | / No | 240
5 | 63 mm dia PVC FTA | 1 | x | 6 | - | - | - | 6 | No's | 30 | / No | 180
6 | 63 mm dia PVC MTA | 1 | x | 6 | - | - | - | 6 | No's | 25 | / No | 150
7 | 63 mm dia PVC ' T ' Bends | 1 | x | 6 | - | - | - | 6 | No's | 50 | / No | 300 | pshaik019@gmail.com
[9 empty] | Sub Total |  |  | 1320
8 | 75 mm dia PVC Bends | 1 | x | 6 | - | - | - | 6 | No's | 40 | / No | 240
9 | 75 mm dia PVC Couplings | 1 | x | 6 | - | - | - | 6 | No's | 25 | / No | 150
10 | 75 mm dia PVC Dummy | 1 | x | 6 | - | - | - | 6 | No's | 25 | / No | 150
11 | 75 mm dia PVC Elbow | 1 | x | 6 | - | - | - | 6 | No's | 55 | / No | 330
12 | 75 mm dia PVC FTA | 1 | x | 6 | - | - | - | 6 | No's | 40 | / No | 240
13 | 75 mm dia PVC MTA | 1 | x | 6 | - | - | - | 6 | No's | 35 | / No | 210
14 | 75 mm dia PVC ' T ' Bends | 1 | x | 6 | - | - | - | 6 | No's | 55 | / No | 330
[9 empty] | Sub Total |  |  | 1650
15 | 90 mm dia PVC Bends | 1 | x | 6 | - | - | - | 6 | No's | 50 | / No | 300
16 | 90 mm dia PVC Couplings | 1 | x | 6 | - | - | - | 6 | No's | 40 | / No | 240
17 | 90 mm dia PVC Dummy | 1 | x | 6 | - | - | - | 6 | No's | 30 | / No | 180
18 | 90 mm dia PVC Elbow | 1 | x | 6 | - | - | - | 6 | No's | 55 | / No | 330
19 | 90 mm dia PVC FTA | 1 | x | 6 | - | - | - | 6 | No's | 55 | / No | 330
20 | 90 mm dia PVC MTA | 1 | x | 6 | - | - | - | 6 | No's | 45 | / No | 270
21 | 90 mm dia PVC ' T ' Bends | 1 | x | 6 | - | - | - | 6 | No's | 80 | / No | 480
[9 empty] | Sub Total |  |  | 2130
22 | Reducer 75 mm to 63 mm | 1 | x | 6 | - | - | - | 6 | No's | 25 | / No | 150
23 | Reducer 90 mm to 63 mm | 1 | x | 6 | - | - | - | 6 | No's | 35 | / No | 210
24 | Reducer 90 mm to 75 mm | 1 | x | 6 | - | - | - | 6 | No's | 40 | / No | 240
25 | 90 mm dia PVC Ball valves | 1 | x | 3 | - | - | - | 3 | No's | 450 | / No | 1350
26 | 75 mm dia PVC Ball valves | 1 | x | 3 | - | - | - | 3 | No's | 350 | / No | 1050
27 | 63 mm dia PVC Ball valves | 1 | x | 3 | - | - | - | 3 | No's | 300 | / No | 900
[9 empty] | Sub Total |  |  | 3900
[9 empty] | Grand Total |  |  | 9000
| Asst. Engineer | [9 empty] | Dy. Executive Engineer,
| RWS & S Thirumalagiri | [9 empty] | RWS & S Sub Division.
Thungathurthy.

## CC Data (hidden)
DATA SHEET FOR LAYING AND JOINTING OF PVC / HDPE PIPES In CC Road Portion
#REF! | #REF! |  | SOR | 2015-2016
#REF! | Name of work :- |  | INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
Earth work excuvation for pipeline trench of the specified size, lowering and laying of PVC pipes, jointing the pipes with each other and with the specials, testing the pipeline with water of required pressure, refilling the trench with excuvated soils watering and tamping etc,.
#REF! | PART - I |  | #REF!
| Earthwork Excavation in all types of soils including refilling by Manual means 1/2 |  |  |  | 112.84 | /1cum | 56.42
| Earthwork Excavation in all types of soils including refilling by Machine 1/2 |  |  |  | 81.28 | /1cum | 40.64
|  |  |  | Average Rate |  |  | 97.06 | /1cum
| Cutting open C.C. road surface | [5 empty] | 1739 | /1cum
PART - II
FOR 63 AND 75 MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 120% for narrow trench |  |  |  | 116.47
[5 empty] | 213.53 | /1cum
With trench size 0.50 X 0.75m
| Cutting open C.C. road surface |  |  | 0.50 X 0.15 X | 1739 |  | 130.42 | /1m
| Excuvation of trench |  |  | 0.50 X 0.60 X | 213.53 |  | 64.05 | /1m
[7 empty] | 194.47 | /1m
| Dia | Trench charge | L & J | #REF! | #REF! |  | #REF! | Total
PVC | 63mm | 194.47 | 6.24 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 75mm | 194.47 | 7.43 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 63mm | 194.47 | 37 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 75mm | 194.47 | 41 | #REF! | #REF! |  | #REF! | #REF! | /1m
FOR 90MM TO 140MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
With trench size 0.70 X 1.00m
| Cutting open C.C. road surface |  |  | 0.70 X 0.15 X | 1739 |  | 182.59 | /1m
| Excuvation of trench |  |  | 0.70 X 0.85 X | 169.85 |  | 101.06 | /1m
[7 empty] | 283.65 | /1m
| Dia | Trench charge | L & J | VAT @ % | #REF! |  | #REF! | Total
PVC | 90mm | 283.65 | 8.91 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 110mm | 283.65 | 10.89 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 125mm | 283.65 | 12.38 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 140mm | 283.65 | 13.86 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 90mm | 283.65 | 46 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 110mm | 283.65 | 53 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 125mm | 283.65 | 64 |  |  |  | #REF! | #REF! | /1m
HDPE | 140mm | 283.65 | 67 | #REF! | #REF! |  | #REF! | #REF! | /1m
| With trench size 0.80 X 1.10m |  |  | 0.80 X 1.10 X | 169.85 |  | 149.46 | /1m
| Dia | Trench charge |  | L & J | #REF! | #REF! |  | Total
PVC | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
PVC | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
FOR 160MM TO 200MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
With trench size 0.80 X 1.10m
| Cutting open C.C. road surface |  |  | 0.80 X 0.15 X | 1739 |  | 208.68 | /1m
| Excuvation of trench |  |  | 0.80 X 0.95 X | 169.85 |  | 129.08 | /1m |  | 0.95
[7 empty] | 337.76 | /1m
| Dia | Trench charge | L & J | VAT @ HDPE% | #REF! |  | #REF! | Total
PVC | 160mm | 337.76 | 15.84 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 180mm | 337.76 | 17.82 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 200mm | 337.76 | 19.8 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 160mm | 337.76 | 72 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 180mm | 337.76 | 80 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 200mm | 337.76 | 87 | #REF! | #REF! |  | #REF! | #REF! | /1m
| With trench size 0.80 X 1.10m |  |  | 0.80 X 1.10 X | 169.85 |  | 149.46 | /1m
| Dia | Trench charge |  | L & J | #REF! | #REF! |  | Total
PVC | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
PVC | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 160mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
HDPE | 180mm | 149.46 |  | #REF! | #REF! | #REF! |  | #REF! | /1m
FOR 200MM TO 315MM PIPES
| Excuvation of trench |  |  |  | 97.06
| Add 75% for narrow trench |  |  |  | 72.79
[5 empty] | 169.85 | /1cum
| With trench size 0.90 X 1.20m | [5 empty] | 0
| Cutting open C.C. road surface |  |  | 0.90 X 0.15X | 1739 |  | 234.76 | /1m
| Excuvation of trench |  |  | 0.90 X 1.05 X | 169.85 |  | 160.5 | /1m |  | 1.05
[7 empty] | 395.26 | /1m
| Dia | Trench charge | L & J | VAT @ HDPE% | #REF! |  | #REF! | Total
PVC | 225mm | 395.26 | 22.28 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 250mm | 395.26 | 24.75 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 280mm | 395.26 | 27.72 | #REF! | #REF! |  | #REF! | #REF! | /1m
PVC | 315mm | 395.26 | 31.19 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 225mm | 395.26 | 96 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 250mm | 395.26 | 102 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 280mm | 395.26 | 112 | #REF! | #REF! |  | #REF! | #REF! | /1m
HDPE | 315mm | 395.26 | 183 | #REF! | #REF! |  | #REF! | #REF! | /1m
| Asst. Engineer |  |  | #REF!
| RWS Thirumalagir |  |  | RWS Subdivision Thungathurthy
Note on A2: Turn Over Tax Percentage
Note on A3: Sundries Operator

## Pipe line (2) (hidden)
Sub Estimate
INTRA VILLAGE SYSTEM FOR PROVIDING DRINKING WATER TO THATIPAMULA H/O THATIPAMULA(V) OF THIRUMALAGIRI(M)
S.No | Description of item | No. | L | B | D | Qty | Unit | Rate | Per | Amount
1 | Supply and Delivery of PVC Pipes 6kg PE 100 grade etc., completed Excluding all Taxes
| 63 mm PVC 6 Kg | 1X1 | 100 |  |  | 100 | Rmt | 74.34 | Rmt | 7434
| 75 mm PVC 6 Kg | 1X1 | 700 |  |  | 700 | Rmt | 101.31 | Rmt | 70917
| 90 mm PVC 6 Kg | 1X1 | 200 |  |  | 200 | Rmt | 146.72 | Rmt | 29344
| 110 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 212.39 | Rmt | 0
| 125 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 270.96 | Rmt | 0
| 140 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 349.54 | Rmt | 0
| 160 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 452.96 | Rmt | 0
| 180 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 583.47 | Rmt | 0
| 200 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 709.61 | Rmt | 0
| 225 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 953.11 | Rmt | 0
| 250 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 1169.47 | Rmt | 0
| 280 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 1477.4 | Rmt | 0
| 315 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | 1856.13 | Rmt | 0
2 | Earth work excuvation for pipeline trench of size 0.50 X 0.75m in all types of soils except hard rock requires blasting ,lowering, laying & jointing PVC pipes ,testing of pipeline ,refilling the trench, watering & tamping of
| 63 mm PVC 6 Kg | 1X1 | 70 |  |  | 70 | Rmt | #REF! | Rmt | #REF!
| 75 mm PVC 6 Kg | 1X1 | 650 |  |  | 650 | Rmt | #REF! | Rmt | #REF!
3 | Earth work excuvation for pipeline trench of size 0.7 X 1m in all types of soils except hard rock requires blasting ,lowering, laying & jointing PVC pipes ,testing of pipeline ,refilling the trench, watering & tamping of
| 90 mm PVC 6 Kg | 1X1 | 100 |  |  | 100 | Rmt | #REF! | Rmt | #REF!
| 110 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 125 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 140 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
4 | Earth work excuvation for pipeline trench of size 0.8 X 1.1m in all types of soils except hard rock requires blasting ,lowering, laying & jointing PVC pipes ,testing of pipeline ,refilling the trench, watering & tamping of
| 160 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 180 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 200 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
5 | Earth work excuvation for pipeline trench of size 0.9 X 1.2m in all types of soils except hard rock requires blasting ,lowering, laying & jointing PVC pipes ,testing of pipeline ,refilling the trench, watering & tamping of
| 225 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 250 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 280 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 315 mm PVC 6 Kg | 1X1 | 0 |  |  | 0 | Rmt | #REF! | Rmt | #REF!
6 | Supply and delivery of Sluice Valves
| '80mm dia on 63mm | 1X3 |  |  |  | 4 | No | 6626 | No | 26504
| '80mm dia on 75mm | 1X5 |  |  |  | 5 | No | 6626 | No | 33130
| '80mm dia on 90mm | 1X2 |  |  |  | 2 | No | 6626 | No | 13252
| '100mm dia on 110mm | 1X1 |  |  |  | 0 | No | 8754 | No | 0
| '125mm dia on 125mm | 1X1 |  |  |  | 0 | No | 8754 | No | 0
| '150mm dia on 140mm | 1X1 |  |  |  | 0 | No | 14316 | No | 0
| 150mm dia on 160mm | 1X1 |  |  |  | 0 | No | 14316 | No | 0
| 150mm dia on 180mm | 1X1 |  |  |  | 0 | No | 14316 | No | 0
| 200mm dia on 200mm | 1X1 |  |  |  | 0 | No | 23072 | No | 0
| 250mm dia on 250mm | 1X1 |  |  |  | 0 | No | 31682 | No | 0
| 300mm dia on 315mm | 1X1 |  |  |  | 0 | No | 53591 | No | 0
7 | Construction of Masonry Sluice valve chembers | 1X11 |  |  |  | 11 | No | 3000 | No | 33000
8 | PVC / CI / GI Specials | As Per Sub Estimate | [7 empty] | 9000
9 | Cutting road surface including stacking of excavated materials for pipe line trench work.
Cutting open C.C. road surface
| 63 mm PVC 6 Kg | 1X1 | 30 |  |  | 30 | Rmt | #REF! | Rmt | #REF!
| 75 mm PVC 6 Kg | 1X1 | 50 |  |  | 50 | Rmt | #REF! | Rmt | #REF!
| 90 mm PVC 6 Kg | 1X1 | 100 |  |  | 100 | Rmt | #REF! | Rmt | #REF!
| 110 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 125 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 140 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 160 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 180 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 200 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 225 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 250 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 280 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
| 315 mm PVC 6 Kg | 1X1 |  |  |  | 0 | Rmt | #REF! | Rmt | #REF!
10 | Providing 15mm dia House Service Connection as per standard specification including the cost of the materials like Clamp Saddle,Ferrule Tapping Saddle confirming to I.S stadard manufactured from virgin resin of PE-80 , Compression Elbows, MDPE PE100 Pipe
|  | 805 |  |  |  | 805 | Each | 1500 | Each | 1207500
12 | ADD CED 12.5% | [8 empty] | 13462
11 | L.S.for U/S Items | L.S.
[8 empty] | TOTAL |  | #REF! | 110000 | 130000
| Asst. Engineer | [5 empty] | Dy. Exe Engineer
| RWS & S Thirumalagiri | [5 empty] | RWS Subdivision Thungathurthy

## Peerya thanda (hidden)
Line From | To | Bearing | Is it new or exists | Material | Length in Mtrs | House Holds | Cum Households | Pop 2011 | Ultimate Population | Demand in Liters @ 100 lpcd | Demand in LPM | Dia required | Provide Dia in MM | Head loss per 1000m | Net head loss in m | HGL @ begin | HGL @ end | GL @ end | Residual head in m | Static Head | Velocity m/sec | Class of Pipe
O | O1 |  | New | PVC | 23 | 4 | 36 | 143 | 210 | 21000 | 87.5 | 59.4 | 90 | 1.067 | 0.02 | 509 | 508.98 | 498 | 10.98 | 14 | 0.22511 | 6 Kg/cm2
O1 | A |  | Exist | PVC | 60 | 6 | 6 | 21 | 30 | 3000 | 12.5 | 24.3 | 63 | 0.175 | 0.01 | 508.98 | 508.97 | 496 | 12.97 | 16 | 0.071475 | 6 Kg/cm2
O1 | B |  | New | PVC | 52 | 8 | 14 | 49 | 72 | 7200 | 30 | 36.3 | 75 | 0.37 | 0.02 | 508.98 | 508.96 | 497 | 11.96 | 15 | 0.12723 | 6 Kg/cm2
O1 | C |  | New | PVC | 76 | 12 | 12 | 42 | 61 | 6100 | 25.4167 | 33.7 | 63 | 0.633 | 0.05 | 508.98 | 508.93 | 500 | 8.93 | 12 | 0.15262 | 6 Kg/cm2
B | B1 |  | New | PVC | 39 | 6 | 6 | 21 | 30 | 3000 | 12.5 | 24.3 | 63 | 0.175 | 0.01 | 508.96 | 508.95 | 495 | 13.95 | 17 | 0.090681 | 6 Kg/cm2

## JALUBAITHANDA (hidden)
Line From | To | Bearing | Is it new or exists | Material | Length in Mtrs | House Holds | Cum Households | Pop 2011 | Ultimate Population | Demand in Liters @ 100 lpcd | Demand in LPM | Dia required | Provide Dia in MM | Head loss per 1000m | Net head loss in m | HGL @ begin | HGL @ end | GL @ end | Residual head in m | Static Head | Velocity m/sec | Class of Pipe
O | O1 |  | New | PVC | 126 | 26 | 26 | 104 | 152 | 15200 | 63.3333 | 51.2 | 90 | 0.595 | 0.07 | 515 | 514.93 | 503 | 11.93 | 15 | 0.17575 | 6 Kg/cm2

## Hydruli stmnt (hidden)
Hydrulic Statement for Intra Village to THATIPAMULA Village of THIRUMALAGIRI Mandal
Line From | To | Bearing | Is it new or exists | Material | Length in Mtrs | House Holds | Cum Households | Pop 2011 | Ultimate Population | Demand in Liters @ 100 lpcd | Demand in LPM | Dia required | Provide Dia in MM | Existing Pipe Dia in MM | Head loss per 1000m | Net head loss in m | HGL @ begin | HGL @ end | GL @ end | Residual head in m | Static Head | Velocity m/sec | Class of Pipe
OHSR (Existing) | 101 |  | New | HDPE | 50 |  | 394 | 1576 | 2111 | 211100 | 586.3889 | 142.6 | 125 | 90 | 6.877 | 0.34 | 252 | 251.66 | 243 | 8.66 | 12 | 0.87035 | 6 Kg/cm2 | 411
101 | 57 |  | New | HDPE | 30 | 2 | 295 | 1180 | 1581 | 158100 | 439.1667 | 124.9 | 110 | 90 | 7.537 | 0.23 | 251.66 | 251.43 | 242.809 | 8.621 | 12.191 | 0.85502 | 6 Kg/cm2
57 | 58 |  | New | HDPE | 70 | 9 | 151 | 604 | 809 | 80900 | 224.7222 | 91.7 | 90 | 90 | 5.885 | 0.41 | 251.43 | 251.02 | 242.755 | 8.265 | 12.245 | 0.64577 | 6 Kg/cm2
58 | 53 |  | New | HDPE | 40 | 6 | 130 | 520 | 696 | 69600 | 193.3333 | 85.6 | 90 | 90 | 4.482 | 0.18 | 251.02 | 250.84 | 242.755 | 8.085 | 12.245 | 0.55825 | 6 Kg/cm2
53 | 51 |  | New | HDPE | 20 | 3 | 111 | 444 | 594 | 59400 | 165 | 79.6 | 90 | 90 | 3.364 | 0.07 | 250.84 | 250.77 | 242.991 | 7.779 | 12.009 | 0.48588 | 6 Kg/cm2
51 | 50 |  | New | HDPE | 20 | 2 | 108 | 432 | 578 | 57800 | 160.5556 | 78.6 | 90 | 90 | 3.202 | 0.06 | 250.77 | 250.71 | 242.864 | 7.846 | 12.136 | 0.44621 | 6 Kg/cm2
50 | 48 |  | New | HDPE | 20 | 2 | 94 | 376 | 503 | 50300 | 139.7222 | 73.7 | 90 | 90 | 2.49 | 0.05 | 250.71 | 250.66 | 242.682 | 7.978 | 12.318 | 0.40345 | 6 Kg/cm2
48 | 49 |  | New | HDPE | 50 | 3 | 92 | 368 | 493 | 49300 | 136.9444 | 73.1 | 90 | 90 | 2.401 | 0.12 | 250.66 | 250.54 | 242.473 | 8.067 | 12.527 | 0.39445 | 6 Kg/cm2
49 | 18 |  | New | HDPE | 30 | 4 | 78 | 312 | 418 | 41800 | 116.1111 | 67.7 | 90 | 90 | 1.781 | 0.05 | 250.54 | 250.49 | 242.378 | 8.112 | 12.622 | 0.32248 | 6 Kg/cm2 | 805
18 | 19 |  | New | HDPE | 40 | 5 | 74 | 296 | 396 | 39600 | 110 | 66 | 90 | 90 | 1.615 | 0.06 | 250.49 | 250.43 | 241.45 | 8.98 | 13.55 | 0.30424 | 6 Kg/cm2
19 | 20 |  | New | HDPE | 30 | 3 | 57 | 228 | 305 | 30500 | 84.7222 | 58.6 | 90 | 90 | 1.007 | 0.03 | 250.43 | 250.4 | 241.395 | 9.005 | 13.605 | 0.24318 | 6 Kg/cm2 | 802
20 | 21 |  | New | HDPE | 50 | 6 | 54 | 216 | 289 | 28900 | 80.2778 | 57.1 | 90 | 90 | 0.913 | 0.05 | 250.4 | 250.35 | 240.875 | 9.475 | 14.125 | 0.24318 | 6 Kg/cm2
21 | 22 |  | New | HDPE | 30 | 3 | 33 | 132 | 176 | 17600 | 48.8889 | 45.5 | 75 | 90 | 0.894 | 0.03 | 250.35 | 250.32 | 240.562 | 9.758 | 14.438 | 0.21571 | 6 Kg/cm2
22 | 24 |  | New | HDPE | 30 | 4 | 30 | 120 | 160 | 16000 | 44.4444 | 43.5 | 75 | 90 | 0.753 | 0.02 | 250.32 | 250.3 | 240.405 | 9.895 | 14.595 | 0.17242 | 6 Kg/cm2
24 | 16 |  | New | HDPE | 70 | 5 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 75 | 90 | 0.028 | 0 | 250.3 | 250.3 | 239.984 | 10.316 | 15.016 | 0 | 6 Kg/cm2
101 | 56 |  | New | HDPE | 30 | 4 | 99 | 396 | 530 | 53000 | 147.2222 | 75.5 | 90 | 90 | 2.737 | 0.08 | 251.66 | 251.58 | 242.823 | 8.757 | 12.177 | 0.4181 | 6 Kg/cm2
56 | 54 |  | New | HDPE | 40 | 5 | 95 | 380 | 509 | 50900 | 141.3889 | 74.1 | 90 | 90 | 2.544 | 0.1 | 251.58 | 251.48 | 242.732 | 8.748 | 12.268 | 0.40345 | 6 Kg/cm2
54 | 55 |  | New | HDPE | 30 | 4 | 90 | 360 | 482 | 48200 | 133.8889 | 72.3 | 90 | 90 | 2.305 | 0.07 | 251.48 | 251.41 | 242.424 | 8.986 | 12.576 | 0.38836 | 6 Kg/cm2
55 | 36 |  | New | HDPE | 40 | 5 | 77 | 308 | 412 | 41200 | 114.4444 | 67.3 | 90 | 90 | 1.735 | 0.07 | 251.41 | 251.34 | 242.246 | 9.094 | 12.754 | 0.33129 | 6 Kg/cm2
36 | 35 |  | New | HDPE | 30 | 5 | 72 | 288 | 385 | 38500 | 106.9444 | 65.2 | 90 | 90 | 1.535 | 0.05 | 251.34 | 251.29 | 242.037 | 9.253 | 12.963 | 0.32248 | 6 Kg/cm2
35 | 34 |  | New | HDPE | 140 | 28 | 59 | 236 | 316 | 31600 | 87.7778 | 59.5 | 90 | 90 | 1.073 | 0.15 | 251.29 | 251.14 | 240.482 | 10.658 | 14.518 | 0.25263 | 6 Kg/cm2
57 | 59 |  | New | HDPE | 20 | 4 | 142 | 568 | 761 | 76100 | 211.3889 | 89.2 | 90 | 90 | 5.268 | 0.11 | 251.43 | 251.32 | 242.809 | 8.511 | 12.191 | 0.62371 | 6 Kg/cm2
59 | 45 |  | New | HDPE | 80 | 8 | 120 | 480 | 643 | 64300 | 178.6111 | 82.5 | 90 | 90 | 3.883 | 0.31 | 251.32 | 251.01 | 243.019 | 7.991 | 11.981 | 0.51398 | 6 Kg/cm2
45 | 43 |  | New | HDPE | 70 | 9 | 84 | 336 | 450 | 45000 | 125 | 70 | 90 | 90 | 2.035 | 0.14 | 251.01 | 250.87 | 243.41 | 7.46 | 11.59 | 0.35665 | 6 Kg/cm2
43 | 44 |  | New | HDPE | 50 | 8 | 61 | 244 | 326 | 32600 | 90.5556 | 60.4 | 75 | 90 | 2.73 | 0.14 | 250.87 | 250.73 | 242.919 | 7.811 | 12.081 | 0.381 | 6 Kg/cm2
45 | 40 |  | Exist | PVC | 59 | 8 | 28 | 112 | 150 | 15000 | 41.6667 | 42.3 | 63 | 90 | 1.549 | 0.09 | 251.01 | 250.92 | 243.314 | 7.606 | 11.686 | 0.24289 | 6 Kg/cm2
40 | 39 |  | Exist | PVC | 46 | 10 | 20 | 80 | 107 | 10700 | 29.7222 | 36.2 | 63 | 90 | 0.841 | 0.04 | 250.92 | 250.88 | 242.379 | 8.501 | 12.621 | 0.17805 | 6 Kg/cm2
39 | 37 |  | Exist | PVC | 11 | 4 | 10 | 40 | 53 | 5300 | 14.7222 | 26.2 | 63 | 90 | 0.236 | 0 | 250.88 | 250.88 | 242.379 | 8.501 | 12.621 | 0 | 6 Kg/cm2
37 | 38 |  | Exist | PVC | 35 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 250.88 | 250.88 | 241.492 | 9.388 | 13.508 | 0 | 6 Kg/cm2
43 | 41 |  | Exist | PVC | 32 | 6 | 14 | 56 | 75 | 7500 | 20.8333 | 30.7 | 63 | 90 | 0.442 | 0.01 | 250.87 | 250.86 | 243.001 | 7.859 | 11.999 | 0.10115 | 6 Kg/cm2
41 | 102 |  | Exist | PVC | 72 | 8 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0.01 | 250.86 | 250.85 | 242.379 | 8.471 | 12.621 | 0.064626 | 6 Kg/cm2
44 | 42 |  | Exist | PVC | 52 | 6 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.02 | 250.73 | 250.71 | 243.23 | 7.48 | 11.77 | 0.11345 | 6 Kg/cm2
42 | 103 |  | Exist | PVC | 66 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0.01 | 250.71 | 250.7 | 243.001 | 7.699 | 11.999 | 0.067808 | 6 Kg/cm2
44 | 61 |  | Exist | PVC | 140 | 12 | 41 | 164 | 219 | 21900 | 60.8333 | 50.3 | 63 | 90 | 3.073 | 0.43 | 250.73 | 250.3 | 242.159 | 8.141 | 12.841 | 0.35755 | 6 Kg/cm2
61 | 62 |  | Exist | PVC | 40 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 250.3 | 250.3 | 242.159 | 8.141 | 12.841 | 0 | 6 Kg/cm2
61 | 63 |  | Exist | PVC | 66 | 9 | 23 | 92 | 123 | 12300 | 34.1667 | 38.6 | 63 | 90 | 1.082 | 0.07 | 250.3 | 250.23 | 241.614 | 8.616 | 13.386 | 0.1987 | 6 Kg/cm2
63 | 64 |  | Exist | PVC | 74 | 2 | 14 | 56 | 75 | 7500 | 20.8333 | 30.7 | 63 | 90 | 0.442 | 0.03 | 250.23 | 250.2 | 241.614 | 8.586 | 13.386 | 0.1168 | 6 Kg/cm2
64 | 100 |  | Exist | PVC | 120 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.04 | 250.2 | 250.16 | 241.614 | 8.546 | 13.386 | 0.10483 | 6 Kg/cm2
59 | 105 |  | Exist | PVC | 123 | 18 | 18 | 72 | 96 | 9600 | 26.6667 | 34.4 | 63 |  | 0.691 | 0.08 | 251.32 | 251.24 | 242.128 | 9.112 | 12.872 | 0.15166 | 6 Kg/cm2
58 | 106 |  | Exist | PVC | 100 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.03 | 251.02 | 250.99 | 242.641 | 8.349 | 12.359 | 0.098899 | 6 Kg/cm2
53 | 107 |  | Exist | PVC | 71 | 13 | 13 | 52 | 69 | 6900 | 19.1667 | 29.6 | 63 | 90 | 0.38 | 0.03 | 250.84 | 250.81 | 242.823 | 7.987 | 12.177 | 0.1195 | 6 Kg/cm2
50 | 108 |  | Exist | PVC | 75 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.02 | 250.71 | 250.69 | 242.732 | 7.958 | 12.268 | 0.092668 | 6 Kg/cm2
49 | 109 |  | Exist | PVC | 91 | 11 | 11 | 44 | 58 | 5800 | 16.1111 | 27.3 | 63 | 90 | 0.277 | 0.03 | 250.54 | 250.51 | 242.424 | 8.086 | 12.576 | 0.10419 | 6 Kg/cm2
19 | 110 |  | Exist | PVC | 113 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.04 | 250.43 | 250.39 | 242.246 | 8.144 | 12.754 | 0.10837 | 6 Kg/cm2
21 | 111 |  | Exist | PVC | 119 | 15 | 15 | 60 | 80 | 8000 | 22.2222 | 31.6 | 63 | 90 | 0.497 | 0.06 | 250.35 | 250.29 | 241.16 | 9.13 | 13.84 | 0.13176 | 6 Kg/cm2
24 | 27 |  | Exist | PVC | 15 | 4 | 21 | 84 | 112 | 11200 | 31.1111 | 36.9 | 63 | 90 | 0.913 | 0.01 | 250.3 | 250.29 | 240.46 | 9.83 | 14.54 | 0.15374 | 6 Kg/cm2
27 | 112 |  | Exist | PVC | 56 | 11 | 11 | 44 | 58 | 5800 | 16.1111 | 27.3 | 63 | 90 | 0.277 | 0.02 | 250.29 | 250.27 | 241.004 | 9.266 | 13.996 | 0.1089 | 6 Kg/cm2
27 | 28 |  | Exist | PVC | 44 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 250.29 | 250.29 | 239.933 | 10.357 | 15.067 | 0 | 6 Kg/cm2
55 | 113 |  | Exist | PVC | 97 | 9 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0.02 | 251.41 | 251.39 | 243.314 | 8.076 | 11.686 | 0.080391 | 6 Kg/cm2
35 | 114 |  | Exist | PVC | 63 | 8 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0.01 | 251.29 | 251.28 | 242.379 | 8.901 | 12.621 | 0.069574 | 6 Kg/cm2
34 | 31 |  | Exist | PVC | 39 | 4 | 31 | 124 | 166 | 16600 | 46.1111 | 44.3 | 63 | 90 | 1.861 | 0.07 | 251.14 | 251.07 | 240.831 | 10.239 | 14.169 | 0.26573 | 6 Kg/cm2
31 | 30 |  | Exist | PVC | 50 | 7 | 18 | 72 | 96 | 9600 | 26.6667 | 34.4 | 63 | 90 | 0.691 | 0.03 | 251.07 | 251.04 | 240.698 | 10.342 | 14.302 | 0.14505 | 6 Kg/cm2
30 | 29 |  | Exist | PVC | 24 | 4 | 11 | 44 | 58 | 5800 | 16.1111 | 27.3 | 63 | 90 | 0.277 | 0.01 | 251.04 | 251.03 | 241.004 | 10.026 | 13.996 | 0.11858 | 6 Kg/cm2
29 | 115 |  | Exist | PVC | 59 | 7 | 7 | 28 | 37 | 3700 | 10.2778 | 22.2 | 63 | 90 | 0.123 | 0.01 | 251.03 | 251.02 | 241.16 | 9.86 | 13.84 | 0.072142 | 6 Kg/cm2
31 | 32 |  | Exist | PVC | 21 | 5 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0 | 251.07 | 251.07 | 241.16 | 9.91 | 13.84 | 0 | 6 Kg/cm2
32 | 33 |  | Exist | PVC | 20 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 251.07 | 251.07 | 241.16 | 9.91 | 13.84 | 0 | 6 Kg/cm2
OHSR (Existing) | OHSR New Jn |  | New | HDPE | 100 |  | 411 | 1644 | 2202 | 220200 | 611.6667 | 145.4 | 125 | 90 | 7.423 | 0.74 | 265.85 | 265.11 | 242.755 | 22.355 | 12.245 | 0.91198 | 6 Kg/cm2
OHSR New Jn | OHSR New 1 |  | New | HDPE | 100 |  | 291 | 1164 | 1559 | 155900 | 433.0556 | 124.1 | 110 | 90 | 7.348 | 0.73 | 265.11 | 264.38 | 242.641 | 21.739 | 12.359 | 0.83218 | 6 Kg/cm2 | 120
OHSR New Jn | OHSR New 2 |  | New | HDPE | 350 |  | 120 | 480 | 643 | 64300 | 178.6111 | 82.5 | 90 | 90 | 3.883 | 1.36 | 265.11 | 263.75 | 242.937 | 20.813 | 12.063 | 0.51477 | 6 Kg/cm2
0
OHSR New 1 | 116 |  | New | HDPE | 100 |  | 291 | 1164 | 1559 | 155900 | 433.0556 | 124.1 | 110 | 90 | 7.348 | 0.73 | 254.641 | 253.911 | 242.641 | 11.27 | 12.359 | 0.83218 | 6 Kg/cm2
116 | 117 |  | New | HDPE | 160 | 8 | 291 | 1164 | 1559 | 155900 | 433.0556 | 124.1 | 110 | 90 | 7.348 | 1.18 | 253.911 | 252.731 | 243.404 | 9.327 | 11.596 | 0.83689 | 6 Kg/cm2
117 | 118 |  | New | HDPE | 30 | 4 | 280 | 1120 | 1500 | 150000 | 416.6667 | 121.9 | 110 | 90 | 6.853 | 0.21 | 252.731 | 252.521 | 242.682 | 9.839 | 12.318 | 0.81311 | 6 Kg/cm2
118 | 11 |  | New | HDPE | 170 | 28 | 261 | 1044 | 1398 | 139800 | 388.3333 | 118 | 110 | 90 | 6.033 | 1.03 | 252.521 | 251.491 | 242.046 | 9.445 | 12.954 | 0.75076 | 6 Kg/cm2
11 | 7 |  | New | HDPE | 30 | 18 | 122 | 488 | 653 | 65300 | 181.3889 | 83.1 | 110 | 90 | 1.521 | 0.05 | 251.491 | 251.441 | 241.401 | 10.04 | 13.599 | 0.36796 | 6 Kg/cm2
7 | 2 |  | New | HDPE | 40 | 12 | 62 | 248 | 332 | 33200 | 92.2222 | 60.9 | 110 | 90 | 0.447 | 0.02 | 251.441 | 251.421 | 242.138 | 9.283 | 12.862 | 0.1892 | 6 Kg/cm2
2 | 1 |  | Exist | PVC | 356 | 7 | 7 | 28 | 37 | 3700 | 10.2778 | 22.2 | 63 | 90 | 0.123 | 0.04 | 251.421 | 251.381 | 240.127 | 11.254 | 14.873 | 0.057484 | 6 Kg/cm2
117 | 129 |  | Exist | PVC | 30 | 3 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 252.731 | 252.731 | 242.565 | 10.166 | 12.435 | 0 | 6 Kg/cm2
118 | 130 |  | Exist | PVC | 44 | 3 | 15 | 60 | 80 | 8000 | 22.2222 | 31.6 | 63 | 90 | 0.497 | 0.02 | 252.521 | 252.501 | 242.4 | 10.101 | 12.6 | 0.12442 | 6 Kg/cm2
130 | 131 |  | New | HDPE | 100 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.03 | 252.501 | 252.471 | 242.182 | 10.289 | 12.818 | 0.098899 | 6 Kg/cm2
11 | 15 |  | Exist | PVC | 57 | 12 | 70 | 280 | 375 | 37500 | 104.1667 | 64.4 | 63 | 90 | 8.136 | 0.46 | 251.491 | 251.031 | 240.968 | 10.063 | 14.032 | 0.60973 | 6 Kg/cm2
15 | 16 |  | Exist | PVC | 46 | 11 | 54 | 216 | 289 | 28900 | 80.2778 | 57.1 | 63 | 90 | 5.077 | 0.23 | 251.031 | 250.801 | 240.519 | 10.282 | 14.481 | 0.46802 | 6 Kg/cm2
16 | 17 |  | Exist | PVC | 61 | 11 | 11 | 44 | 58 | 5800 | 16.1111 | 27.3 | 63 | 90 | 0.277 | 0.02 | 250.3 | 250.28 | 239.655 | 10.625 | 15.345 | 0.10387 | 6 Kg/cm2
7 | 8 |  | Exist | PVC | 54 | 12 | 42 | 168 | 225 | 22500 | 62.5 | 50.9 | 63 | 90 | 3.227 | 0.17 | 251.441 | 251.271 | 240.954 | 10.317 | 14.046 | 0.36246 | 6 Kg/cm2
8 | 9 |  | Exist | PVC | 45 | 10 | 25 | 100 | 134 | 13400 | 37.2222 | 40.1 | 63 | 90 | 1.263 | 0.06 | 251.271 | 251.211 | 240.431 | 10.78 | 14.569 | 0.22548 | 6 Kg/cm2
9 | 10 |  | Exist | PVC | 69 | 9 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0.01 | 251.211 | 251.201 | 239.707 | 11.494 | 15.293 | 0.066163 | 6 Kg/cm2
2 | 4 |  | Exist | PVC | 50 | 11 | 33 | 132 | 176 | 17600 | 48.8889 | 45.5 | 63 | 90 | 2.069 | 0.1 | 251.421 | 251.321 | 241.083 | 10.238 | 13.917 | 0.2821 | 6 Kg/cm2
4 | 5 |  | Exist | PVC | 45 | 10 | 22 | 88 | 117 | 11700 | 32.5 | 37.7 | 63 | 90 | 0.988 | 0.04 | 251.321 | 251.281 | 240.59 | 10.691 | 14.41 | 0.18023 | 6 Kg/cm2
5 | 6 |  | Exist | PVC | 72 | 12 | 12 | 48 | 64 | 6400 | 17.7778 | 28.6 | 63 | 90 | 0.332 | 0.02 | 251.281 | 251.261 | 239.71 | 11.551 | 15.29 | 0.094782 | 6 Kg/cm2
15 | 121 |  | Exist | PVC | 33 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 251.031 | 251.031 | 240.954 | 10.077 | 14.046 | 0 | 6 Kg/cm2
16 | 122 |  | Exist | PVC | 34 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 250.3 | 250.3 | 240.431 | 9.869 | 14.569 | 0 | 6 Kg/cm2
8 | 123 |  | Exist | PVC | 35 | 5 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 63 | 90 | 0.065 | 0 | 251.271 | 251.271 | 241.083 | 10.188 | 13.917 | 0 | 6 Kg/cm2
9 | 124 |  | Exist | PVC | 37 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 251.211 | 251.211 | 240.59 | 10.621 | 14.41 | 0 | 6 Kg/cm2
11 | 12 |  | Exist | PVC | 46 | 4 | 41 | 164 | 219 | 21900 | 60.8333 | 50.3 | 63 | 90 | 3.073 | 0.14 | 251.491 | 251.351 | 242.058 | 9.293 | 12.942 | 0.35575 | 6 Kg/cm2
12 | 13 |  | Exist | PVC | 42 | 6 | 27 | 108 | 144 | 14400 | 40 | 41.5 | 63 | 90 | 1.439 | 0.06 | 251.351 | 251.291 | 242.182 | 9.109 | 12.818 | 0.23424 | 6 Kg/cm2
13 | 60 |  | Exist | PVC | 62 | 11 | 11 | 44 | 58 | 5800 | 16.1111 | 27.3 | 63 | 90 | 0.277 | 0.02 | 251.291 | 251.271 | 242.069 | 9.202 | 12.931 | 0.10294 | 6 Kg/cm2
13 | 14 |  | Exist | PVC | 46 | 6 | 10 | 40 | 53 | 5300 | 14.7222 | 26.2 | 63 | 90 | 0.236 | 0.01 | 251.291 | 251.281 | 242.06 | 9.221 | 12.94 | 0.082777 | 6 Kg/cm2
14 | 128 |  | Exist | PVC | 29 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 251.281 | 251.281 | 242.034 | 9.247 | 12.966 | 0 | 6 Kg/cm2
12 | 125 |  | Exist | PVC | 40 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 251.351 | 251.351 | 242.034 | 9.317 | 12.966 | 0 | 6 Kg/cm2
2 | 3 |  | Exist | PVC | 44 | 6 | 10 | 40 | 53 | 5300 | 14.7222 | 26.2 | 63 | 90 | 0.236 | 0.01 | 251.421 | 251.411 | 241.878 | 9.533 | 13.122 | 0.084835 | 6 Kg/cm2
3 | 127 |  | Exist | PVC | 28 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 251.411 | 251.411 | 242.034 | 9.377 | 12.966 | 0 | 6 Kg/cm2
16 | 23 |  | Exist | PVC | 65 | 9 | 28 | 112 | 150 | 15000 | 41.6667 | 42.3 | 63 | 90 | 1.549 | 0.1 | 250.3 | 250.2 | 240.458 | 9.742 | 14.542 | 0.24403 | 6 Kg/cm2
23 | 119 |  | Exist | PVC | 25 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 250.2 | 250.2 | 240.562 | 9.638 | 14.438 | 0 | 6 Kg/cm2
23 | 25 |  | Exist | PVC | 23 | 6 | 13 | 52 | 69 | 6900 | 19.1667 | 29.6 | 63 | 90 | 0.38 | 0.01 | 250.2 | 250.19 | 240.216 | 9.974 | 14.784 | 0.1214 | 6 Kg/cm2
12 | 46 |  | Exist | PVC | 43 | 6 | 6 | 24 | 32 | 3200 | 8.8889 | 20.8 | 63 | 90 | 0.095 | 0 | 251.351 | 251.351 | 242.076 | 9.275 | 12.924 | 0 | 6 Kg/cm2
25 | 126 |  | Exist | PVC | 32 | 7 | 7 | 28 | 37 | 3700 | 10.2778 | 22.2 | 63 | 90 | 0.123 | 0 | 250.19 | 250.19 | 240.405 | 9.785 | 14.595 | 0 | 6 Kg/cm2
OHSR New 2 | 74 |  | New | HDPE | 100 |  | 120 | 480 | 643 | 64300 | 178.6111 | 82.5 | 90 | 90 | 3.883 | 0.39 | 254.937 | 254.547 | 242.482 | 12.065 | 12.518 | 0.51581 | 6 Kg/cm2
74 | 97 |  | Exist | PVC | 68 | 3 | 99 | 396 | 530 | 53000 | 147.2222 | 75.5 | 75 | 90 | 6.579 | 0.45 | 254.547 | 254.097 | 242.125 | 11.972 | 12.875 | 0.61278 | 6 Kg/cm2
97 | 132 |  | Exist | PVC | 34 | 4 | 87 | 348 | 466 | 46600 | 129.4444 | 71.2 | 75 | 90 | 5.212 | 0.18 | 254.097 | 253.917 | 242.125 | 11.792 | 12.875 | 0.54171 | 6 Kg/cm2 | 411
132 | 133 |  | Exist | PVC | 74 | 6 | 83 | 332 | 444 | 44400 | 123.3333 | 69.6 | 75 | 90 | 4.775 | 0.35 | 253.917 | 253.567 | 241.614 | 11.953 | 13.386 | 0.509 | 6 Kg/cm2
133 | 66 |  | Exist | PVC | 59 | 3 | 77 | 308 | 412 | 41200 | 114.4444 | 67.3 | 75 | 90 | 4.17 | 0.25 | 253.567 | 253.317 | 241.317 | 12 | 13.683 | 0.479 | 6 Kg/cm2
66 | 67 |  | Exist | PVC | 16 | 3 | 71 | 284 | 380 | 38000 | 105.5556 | 64.8 | 75 | 90 | 3.602 | 0.06 | 253.317 | 253.257 | 241.476 | 11.781 | 13.524 | 0.44773 | 6 Kg/cm2
67 | 68 |  | Exist | PVC | 52 | 3 | 64 | 256 | 343 | 34300 | 95.2778 | 61.8 | 75 | 90 | 2.993 | 0.16 | 253.257 | 253.097 | 242.044 | 11.053 | 12.956 | 0.40138 | 6 Kg/cm2
68 | 79 |  | Exist | PVC | 38 | 3 | 45 | 180 | 241 | 24100 | 66.9444 | 52.6 | 75 | 90 | 1.58 | 0.06 | 253.097 | 253.037 | 240.405 | 12.632 | 14.595 | 0.27763 | 6 Kg/cm2
79 | 83 |  | Exist | PVC | 34 | 3 | 34 | 136 | 182 | 18200 | 50.5556 | 46.2 | 63 | 90 | 2.199 | 0.07 | 253.037 | 252.967 | 242.317 | 10.65 | 12.683 | 0.28665 | 6 Kg/cm2
83 | 88 |  | Exist | PVC | 49 | 3 | 27 | 108 | 144 | 14400 | 40 | 41.5 | 63 | 90 | 1.439 | 0.07 | 252.967 | 252.897 | 242.317 | 10.58 | 12.683 | 0.23424 | 6 Kg/cm2
88 | 87 |  | Exist | PVC | 39 | 2 | 21 | 84 | 112 | 11200 | 31.1111 | 36.9 | 63 | 90 | 0.913 | 0.04 | 252.897 | 252.857 | 243.612 | 9.245 | 11.388 | 0.19505 | 6 Kg/cm2
87 | 91 |  | Exist | PVC | 67 | 3 | 13 | 52 | 69 | 6900 | 19.1667 | 29.6 | 63 | 90 | 0.38 | 0.03 | 252.857 | 252.827 | 244.308 | 8.519 | 10.692 | 0.12339 | 6 Kg/cm2
91 | 93 |  | Exist | PVC | 44 | 2 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0.01 | 252.827 | 252.817 | 244.653 | 8.164 | 10.347 | 0.084835 | 6 Kg/cm2
93 | 95 |  | Exist | PVC | 27 | 1 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 63 | 90 | 0.065 | 0 | 252.817 | 252.817 | 244.631 | 8.186 | 10.369 | 0 | 6 Kg/cm2
95 | 96 |  | Exist | PVC | 325 | 2 | 2 | 8 | 10 | 1000 | 2.7778 | 12.2 | 63 | 90 | 0.012 | 0 | 252.817 | 252.817 | 245.636 | 7.181 | 9.364 | 0 | 6 Kg/cm2
74 | 76 |  | Exist | PVC | 35 | 4 | 17 | 68 | 91 | 9100 | 25.2778 | 33.6 | 63 | 90 | 0.627 | 0.02 | 254.547 | 254.527 | 242.713 | 11.814 | 12.287 | 0.14119 | 6 Kg/cm2
76 | 81 |  | Exist | PVC | 35 | 1 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0.01 | 254.527 | 254.517 | 242.891 | 11.626 | 12.109 | 0.096268 | 6 Kg/cm2
81 | 84 |  | Exist | PVC | 43 | 3 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0.01 | 254.517 | 254.507 | 243.152 | 11.355 | 11.848 | 0.085919 | 6 Kg/cm2
84 | 85 |  | Exist | PVC | 35 | 4 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 63 | 90 | 0.065 | 0 | 254.507 | 254.507 | 242.922 | 11.585 | 12.078 | 0 | 6 Kg/cm2
85 | 86 |  | Exist | PVC | 37 | 1 | 1 | 4 | 5 | 500 | 1.3889 | 8.8 | 63 | 90 | 0.003 | 0 | 254.507 | 254.507 | 243.088 | 11.419 | 11.912 | 0 | 6 Kg/cm2
74 | 75 |  | Exist | PVC | 39 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 254.547 | 254.547 | 242.741 | 11.806 | 12.259 | 0 | 6 Kg/cm2
76 | 80 |  | New | HDPE | 110 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 254.527 | 254.527 | 242.67 | 11.857 | 12.33 | 0 | 6 Kg/cm2
66 | 71 |  | Exist | PVC | 24 | 1 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 253.317 | 253.317 | 241.855 | 11.462 | 13.145 | 0 | 6 Kg/cm2
67 | 72 |  | Exist | PVC | 41 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 253.257 | 253.257 | 241.604 | 11.653 | 13.396 | 0 | 6 Kg/cm2
71 | 141 |  | Exist | PVC | 36 | 2 | 2 | 8 | 10 | 1000 | 2.7778 | 12.2 | 63 | 90 | 0.012 | 0 | 253.317 | 253.317 | 241.604 | 11.713 | 13.396 | 0 | 6 Kg/cm2
97 | 98 |  | Exist | PVC | 10 | 1 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0 | 254.097 | 254.097 | 242.125 | 11.972 | 12.875 | 0 | 6 Kg/cm2
98 | 99 |  | Exist | PVC | 104 | 3 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0.02 | 254.097 | 254.077 | 242.477 | 11.6 | 12.523 | 0.077355 | 6 Kg/cm2
99 | 100 |  | Exist | PVC | 41 | 4 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 63 | 90 | 0.065 | 0 | 254.077 | 254.077 | 242.641 | 11.436 | 12.359 | 0 | 6 Kg/cm2
100 | 142 |  | Exist | PVC | 104 | 1 | 1 | 4 | 5 | 500 | 1.3889 | 8.8 | 63 | 90 | 0.003 | 0 | 250.16 | 250.16 | 242.128 | 8.032 | 12.872 | 0 | 6 Kg/cm2
68 | 70 |  | Exist | PVC | 30 | 3 | 16 | 64 | 85 | 8500 | 23.6111 | 32.5 | 63 | 90 | 0.554 | 0.02 | 253.097 | 253.077 | 242.188 | 10.889 | 12.812 | 0.15374 | 6 Kg/cm2
70 | 73 |  | Exist | PVC | 28 | 1 | 9 | 36 | 48 | 4800 | 13.3333 | 25 | 63 | 90 | 0.197 | 0.01 | 253.077 | 253.067 | 242.29 | 10.777 | 12.71 | 0.1089 | 6 Kg/cm2
73 | 143 |  | Exist | PVC | 32 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 253.067 | 253.067 | 242.482 | 10.585 | 12.518 | 0 | 6 Kg/cm2
79 | 78 |  | Exist | PVC | 31 | 1 | 8 | 32 | 42 | 4200 | 11.6667 | 23.5 | 63 | 90 | 0.155 | 0 | 253.037 | 253.037 | 242.094 | 10.943 | 12.906 | 0 | 6 Kg/cm2
78 | 77 |  | Exist | PVC | 30 | 3 | 7 | 28 | 37 | 3700 | 10.2778 | 22.2 | 63 | 90 | 0.123 | 0 | 253.037 | 253.037 | 242.557 | 10.48 | 12.443 | 0 | 6 Kg/cm2
77 | 144 |  | Exist | PVC | 37 | 3 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 253.037 | 253.037 | 242.703 | 10.334 | 12.297 | 0 | 6 Kg/cm2
83 | 82 |  | Exist | PVC | 61 | 1 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 252.967 | 252.967 | 242.703 | 10.264 | 12.297 | 0 | 6 Kg/cm2
82 | 145 |  | Exist | PVC | 33 | 3 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 252.967 | 252.967 | 242.891 | 10.076 | 12.109 | 0 | 6 Kg/cm2
70 | 146 |  | Exist | PVC | 35 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 253.077 | 253.077 | 242.094 | 10.983 | 12.906 | 0 | 6 Kg/cm2
73 | 147 |  | Exist | PVC | 34 | 4 | 4 | 16 | 21 | 2100 | 5.8333 | 17.1 | 63 | 90 | 0.044 | 0 | 253.067 | 253.067 | 242.557 | 10.51 | 12.443 | 0 | 6 Kg/cm2
77 | 148 |  | Exist | PVC | 34 | 1 | 1 | 4 | 5 | 500 | 1.3889 | 8.8 | 63 | 90 | 0.003 | 0 | 253.037 | 253.037 | 242.703 | 10.334 | 12.297 | 0 | 6 Kg/cm2
88 | 149 |  | Exist | PVC | 65 | 3 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 252.897 | 252.897 | 242.922 | 9.975 | 12.078 | 0 | 6 Kg/cm2
87 | 90 |  | Exist | PVC | 39 | 2 | 5 | 20 | 26 | 2600 | 7.2222 | 18.9 | 63 | 90 | 0.065 | 0 | 252.857 | 252.857 | 242.534 | 10.323 | 12.466 | 0 | 6 Kg/cm2
90 | 92 |  | Exist | PVC | 67 | 3 | 3 | 12 | 16 | 1600 | 4.4444 | 15.1 | 63 | 90 | 0.027 | 0 | 252.857 | 252.857 | 243.215 | 9.642 | 11.785 | 0 | 6 Kg/cm2
91 | 139 |  | Exist | PVC | 39 | 2 | 2 | 8 | 10 | 1000 | 2.7778 | 12.2 | 63 | 90 | 0.012 | 0 | 252.827 | 252.827 | 244.308 | 8.519 | 10.692 | 0 | 6 Kg/cm2
93 | 94 |  | Exist | PVC | 81 | 1 | 1 | 4 | 5 | 500 | 1.3889 | 8.8 | 63 | 90 | 0.003 | 0 | 252.817 | 252.817 | 243.213 | 9.604 | 11.787 | 0 | 6 Kg/cm2
95 | 140 |  | Exist | PVC | 84 | 2 | 2 | 8 | 10 | 1000 | 2.7778 | 12.2 | 63 | 90 | 0.012 | 0 | 252.817 | 252.817 | 243.213 | 9.604 | 11.787 | 0 | 6 Kg/cm2
87 | 150 |  | Exist | PVC | 56 | 1 | 1 | 4 | 5 | 500 | 1.3889 | 8.8 | 63 | 90 | 0.003 | 0 | 252.857 | 252.857 | 243.088 | 9.769 | 11.912 | 0 | 6 Kg/cm2
Asst. Engineer | [19 empty] | Dy. Exe Engineer
RWS & S Thirumalagiri | [19 empty] | RWS Subdivision Thungathurthy
Executive Engineer | [19 empty] | Superintending Engineer
RWS&S Div-I Nalgonda | [19 empty] | RWS&S Circle Nalgonda

## Sheet1 (hidden)
House Holds
10 KL | 42 | 168 | 200 | 10000
20 KL | 84 | 336 | 400 | 20000
40 KL | 168 | 672 | 801 | 40050
60 KL | 252 | 1008 | 1201 | 60050
100 KL | 420 | 1680 | 2002 | 100100
200 KL | 840 | 3360 | 4004 | 200200
300 KL | 1260 | 5040 | 6006 | 300300
| 63 | 57.5
| 75 | 68.7
| 90 | 82.4
| 110 | 100.7
| 125 | 114.5
| 140 | 128.4
| 160 | 148
| 250 | 225.8
| 280 | 252.9
| 315 | 284.5

## Sheet2 (hidden)
| 14-15 | 13-14 | 12-13
Earthwork Excavation in all types of soils including refilling by Manual means | 107.38 | 101.92 | 91 | 107.38 | 101.92 | 91
Earthwork Excavation in all types of soils including refilling by Machine | 81.44 | 78.57 | 73.67
| Diff | 5.46 | 10.92
| Diff | 2.87 | 4.9
L/J
63 | 5.99 | 5.61 | 5.17
75 | 7.13 | 6.68 | 6.15
90 | 8.55 | 8.01 | 7.38
110 | 10.45 | 9.79 | 9.02
140 | 13.3 | 12.46 | 11.48
160 | 15.2 | 14.24 | 13.12
180 | 17.1 | 16.02 | 14.76
| Diff | 0.38 | 0.44
| Diff | 0.45 | 0.53
| Diff | 0.54 | 0.63
| Diff | 0.66 | 0.77
| Diff | 0.84 | 0.98
| Diff | 0.96 | 1.12
| Diff | 1.08 | 1.26

## ew OG 10 KG
Data based on 2025-26 Common SSR
[7 empty] | MA | 0%
| Earthwork excavation in all soils upto SDR using 1/3 machinery and 2/3rd manual labour | [11 empty] | Common SSR | 2025-26
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | 102.8533 | - | 102.8533 | Cost of sand for filling |  | - |  | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead |  | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 |  | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 0 | - | 0 | Filling charges |  | - |  | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | 220.22 |  | 220.22 | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  |  | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 1/3rd machinery & 2/3rd manual |  | 181.1 | /cum |  |  | Total: | 0 |  |  |  |  | Total: | 220.22 |  |  | 313.0702
|  | Extra Allowance for trench cutting |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | 220.22
| PVC pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 82 | 112 | 163 | 233 | 298 | 383 | 498 | 640 | 780 | 1048 | 1284 | 1621 | 2037 | 0 | 0 |  |  | P NO:688 | 6KG
|  | Total | 82 | 112 | 163 | 233 | 298 | 383 | 498 | 640 | 780 | 1048 | 1284 | 1621 | 2037
PVC pipes - Earth work-Part-B
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 235.43 | 235.43
2 | Extra allowance at 75% |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | 10.58 | 12.6 | 15.12 | 18.48 | 21 | 23.52 | 26.88 | 30.24 | 33.6 | 37.8 | 42 | 47.04 | 52.92
6 | Cost of specials (1.20%) with same pressure gauge |  | 0.984 | 1.344 | 1.956 | 2.796 | 3.576 | 4.596 | 5.976 | 7.68 | 9.36 | 12.576 | 15.408 | 19.452 | 24.444
6 | Add CF 13.615% |  | 29.3286 | 29.6527 | 30.0791 | 30.6509 | 31.1002 | 31.5822 | 39.3645 | 40.054 | 40.7402 | 49.6792 | 50.6366 | 51.8734 | 53.3536 | 48.2448 | 48.2448 | 0 | 0 | 355.0773 | 426092.8
|  | Total | 244.74 | 247.45 | 251.01 | 255.78 | 259.53 | 263.55 | 328.49 | 334.24 | 339.97 | 414.57 | 422.55 | 432.88 | 445.23
|  | 25% Muncipal/Agency allowance for Earth work | 28.3373 | 28.8423 | 29.4723 | 29.0383 | 30.9423 | 30.2983 | 37.4173 | 38.2573 | 40.6989 | 49.0896 | 50.1396 | 51.3996 | 52.8696 | 16.9867 | 16.9867 | 16.9867 | 16.9867 | 388.2923 | 582438.5
|  | Total: | 273.0773 | 276.2923 | 280.4823 | 284.8183 | 290.4723 | 293.8483 | 365.9073 | 372.4973 | 380.6689 | 463.6596 | 472.6896 | 484.2796 | 498.0996
| HDPE pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 150 | 214 | 302 | 446 | 581 | 727 | 952 | 1202 | 1478 | 1923 | 2370 | 3005 | 3758 | 0 | 0 |  |  |  | 10 KG | P-678
|  | Total | 150 | 214 | 302 | 446 | 581 | 727 | 952 | 1202 | 1478 | 1923 | 2370 | 3005 | 3758
HDPE pipes - Earth work - Part-B
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 253.54 | 253.54 | 253.54
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 77.08 | 77.08 | 77.08
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing, Pg N0 610 |  | 46 | 50 | 59 | 72 | 86 | 92 | 99 | 108 | 117 | 132 | 139 | 152 | 237 | 204 | 227 | 252
| Cost of specials (0.50%) with same pressure gauge |  | 0.75 | 1.07 | 1.51 | 2.23 | 2.905 | 3.635 | 4.76 | 6.01 | 7.39 | 9.615 | 11.85 | 15.025 | 18.79
5 | Add CF 13.615% |  | 34.1192 | 34.7074 | 35.9926 | 37.8606 | 39.8586 | 40.7749 | 49.0181 | 50.4136 | 51.8269 | 62.1014 | 63.3588 | 65.561 | 77.6463 | 0 | 0 | 0
|  | Total | 284.72 | 289.63 | 300.35 | 315.94 | 332.61 | 340.26 | 409.05 | 420.69 | 432.49 | 518.23 | 528.72 | 547.1 | 647.95 | 534.62 | 557.62 | 582.62
|  | Agency Allowance 25% | 37.1923 | 38.1923 | 40.4423 | 43.6923 | 47.1923 | 48.6923 | 57.0489 | 59.2989 | 61.5489 | 70.6754 | 74.3896 | 77.6396 | 98.8896
|  | TOTAL | 321.9123 | 327.8223 | 340.7923 | 359.6323 | 379.8023 | 388.9523 | 466.0989 | 479.9889 | 494.0389 | 588.9054 | 603.1096 | 624.7396 | 746.8396
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 608.496 | 941.72
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 286.29
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | 560.62 | 596.62 | 698.64 | 829.75 | 960.6 | 1090.18 | 1214.47 | 1377.48 | 1884.01
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 636.62 | 690.62 | 756.62 | 806.62 | 1011.64 | 1214.75 | 1406.6 | 1599.18 | 1850.47 | 2026.5 | 2375.58 | 4820.73
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | 266.6697 | 289.76 | 313.7557 | 338.657 | 391.176 | 447.317 | 507.08 | 570.465 | 637.472 | #VALUE!
2 | Extra allowance |  | 81.07 | 88.09 | 95.38 | 102.95 | 118.92 | 135.99 | 154.15 | 173.42 | 193.79 | 0
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 507.08 | 507.08 | 570.465 | 570.465 | 666.448
2 | Extra allowance |  | 59.46 | 59.46 | 59.46 | 59.46 | 64.41 | 64.41 | 64.41 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31 | 128.83 | 154.15 | 154.15 | 173.42 | 173.42 | 202.6
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | 255.048 | 255.048 | 255.048 | 255.048 | 276.297 | 276.297 | 276.297 | 330.62 | 330.62 | 357.7164 | 415.636 | 481.754 | 552.604 | 661.23 | 661.23 | 743.885 | 743.885 | 869.048
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 290.048 | 307.048 | 312.048 | 323.048 | 365.297 | 383.297 | 408.297 | 554.62 | 666.62 | 766.7164 | 935.636 | 1040.754 | 1176.604 | 1355.23 | 1391.23 | 1522.885 | 1593.885 | 1744.048
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444
| 2 | Extra allowance | 59.46 | 59.46 | 21.66 | 59.46 | 64.41 | 64.41 | 21.66 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31
| 3 | Sand cushion cost | 0 | 0 | 0 | 0 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352 | 860.225 | 941.72 | 1026.837 | 1115.576 | 1207.937 | 1303.92 | 1403.525 | 1506.752
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 636.62 | 690.62 | 779.62 | 858.62 | 990.64 | 1154.75 | 1319.6 | 1508.18 | 1700.47 | 1851.5 | 2124.58 | 4504.73 | 4677.61 | 4904.1 | 5163.22 | 5396.96 | 5729.32 | 5954.3 | 6259.91 | 6523.13
Note on J7: to be changed based on the corresponding lead from master copy

## ew OG 6 KG
Data based on 2025-26 Common SSR
[7 empty] | MA | 0%
| Earthwork excavation in all soils upto SDR using 1/3 machinery and 2/3rd manual labour | [11 empty] | Common SSR | 2025-26
|  | Rate Analysis : | Rate | Add: LI 13% | Total | Sand for bedding/encasing: |  |  | Rate |  | Earth work classification : | Earth work classification : |  |  | Rate/cum
| 1 | E/W Rate -using machinery | 102.8533 | - | 102.8533 | Cost of sand for filling |  | - |  | 1 | Sand or Loose soils wet sand(8b) | Sand or Loose soils wet sand(8b)
| 2 | Diff. of 20a & 20b (of 8,9,12,13) |  | 0 | 0 | Conveyance charges |  | 10KM Lead |  | 2 | Loamy clayey soils like BC and OG soils (9b) | Loamy clayey soils like BC and OG soils (9b) | [5 empty] | 84.1
| 3 | Cost of refilling | included in e/w |  | 0 | Seignorage charges |  | 40/1.13615 |  | 3 | Slushy Soils (10b) | Slushy Soils (10b) | [5 empty] | 126 | 35.2066
| 4 | Cost of sand filling | 0 | - | 0 | Filling charges |  | - |  | 4 | Clayey Soils(11b) | Clayey Soils(11b) | [5 empty] | 210.1
| 5 | E/W rate - manual(as per Std. data) | 220.22 |  | 220.22 | Deduct stacking |  | stacking |  | 5 | Hard gravelly soils (12b) | Hard gravelly soils (12b) | [5 empty] | 146.8
[6 empty] | Add: MA on filling charges |  |  |  | 6 | Mixture of gravel and SDR (13b) | Mixture of gravel and SDR (13b) | [5 empty] | 356.9
|  | E/w rate for 1/3rd machinery & 2/3rd manual |  | 181.1 | /cum |  |  | Total: | 0 |  |  |  |  | Total: | 220.22 |  |  | 313.0702
|  | Extra Allowance for trench cutting |  | 75% | [9 empty] | Add LA & LI at 13%
[14 empty] | Average Manual earth work rate with LA & LI - per cum: | 220.22
| PVC pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 82 | 112 | 163 | 233 | 298 | 383 | 498 | 640 | 780 | 1048 | 1284 | 1621 | 2037 | 0 | 0 |  |  | P NO:688 | 6KG
|  | Total | 82 | 112 | 163 | 233 | 298 | 383 | 498 | 640 | 780 | 1048 | 1284 | 1621 | 2037
PVC pipes - Earth work-Part-B
1 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for P.V.C pipes with 150 mm thick sand cushion and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0mx1.3m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 235.43 | 235.43
2 | Extra allowance at 75% |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92 | 118.92
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Lowering, Laying, Jointing & HF testing |  | 10.58 | 12.6 | 15.12 | 18.48 | 21 | 23.52 | 26.88 | 30.24 | 33.6 | 37.8 | 42 | 47.04 | 52.92
6 | Cost of specials (1.20%) with same pressure gauge |  | 0.984 | 1.344 | 1.956 | 2.796 | 3.576 | 4.596 | 5.976 | 7.68 | 9.36 | 12.576 | 15.408 | 19.452 | 24.444
6 | Add CF 13.615% |  | 29.3286 | 29.6527 | 30.0791 | 30.6509 | 31.1002 | 31.5822 | 39.3645 | 40.054 | 40.7402 | 49.6792 | 50.6366 | 51.8734 | 53.3536 | 48.2448 | 48.2448 | 0 | 0 | 355.0773 | 426092.8
|  | Total | 244.74 | 247.45 | 251.01 | 255.78 | 259.53 | 263.55 | 328.49 | 334.24 | 339.97 | 414.57 | 422.55 | 432.88 | 445.23
|  | 25% Muncipal/Agency allowance for Earth work | 28.3373 | 28.8423 | 29.4723 | 29.0383 | 30.9423 | 30.2983 | 37.4173 | 38.2573 | 40.6989 | 49.0896 | 50.1396 | 51.3996 | 52.8696 | 16.9867 | 16.9867 | 16.9867 | 16.9867 | 388.2923 | 582438.5
|  | Total: | 273.0773 | 276.2923 | 280.4823 | 284.8183 | 290.4723 | 293.8483 | 365.9073 | 372.4973 | 380.6689 | 463.6596 | 472.6896 | 484.2796 | 498.0996
| HDPE pipes -Materail component-Part-A |  |  |  | For the month of November 2017
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355mm | 400mm
1 | Pipe cost |  | 101 | 141 | 203 | 341 | 396 | 494 | 650 | 815 | 1016 | 1302 | 1608 | 2008 | 2537 | 0 | 0 |  |  |  | 6 KG | P-678
|  | Total | 101 | 141 | 203 | 341 | 396 | 494 | 650 | 815 | 1016 | 1302 | 1608 | 2008 | 2537
HDPE pipes - Earth work - Part-B
2 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for HDPE pipes filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.70m x 1.00m | [5 empty] | 0.80m x 1.10m |  |  | 0.90m x 1.20m |  |  |  | 1.0m x 1.40m
| Pipe dia in mm = |  | 63 | 75 | 90 | 110 | 125 | 140 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 355 | 400 | 450
1 | Earth work |  | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 126.77 | 159.37 | 159.37 | 159.37 | 195.59 | 195.59 | 195.59 | 195.59 | 253.54 | 253.54 | 253.54
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 96.9 | 96.9 | 118.92 | 118.92 | 118.92 | 118.92 | 77.08 | 77.08 | 77.08
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, Jointing & H F Testing, Pg N0 610 |  | 46 | 50 | 59 | 72 | 86 | 92 | 99 | 108 | 117 | 132 | 139 | 152 | 237 | 204 | 227 | 252
| Cost of specials (0.50%) with same pressure gauge |  | 0.505 | 0.705 | 1.015 | 1.705 | 1.98 | 2.47 | 3.25 | 4.075 | 5.08 | 6.51 | 8.04 | 10.04 | 12.685
5 | Add CF 13.615% |  | 34.0858 | 34.6577 | 35.9252 | 37.7891 | 39.7327 | 40.6163 | 48.8125 | 50.1502 | 51.5124 | 61.6787 | 62.84 | 64.8823 | 76.8151 | 0 | 0 | 0
|  | Total | 284.44 | 289.21 | 299.79 | 315.34 | 331.56 | 338.94 | 407.33 | 418.5 | 429.86 | 514.7 | 524.39 | 541.43 | 641.01 | 534.62 | 557.62 | 582.62
|  | Agency Allowance 25% | 37.1923 | 38.1923 | 40.4423 | 43.6923 | 47.1923 | 48.6923 | 57.0489 | 59.2989 | 61.5489 | 70.6754 | 74.3896 | 77.6396 | 98.8896
|  | TOTAL | 321.6323 | 327.4023 | 340.2323 | 359.0323 | 378.7523 | 387.6323 | 464.3789 | 477.7989 | 491.4089 | 585.3754 | 598.7796 | 619.0696 | 739.8996
PSC pipes - Earth work
3 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for PSC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.1m x 1.6m | 1.2m x 1.7m | 1.3m x 1.8m | 1.4m x 1.9m | 1.5m x 2.0m | 1.6m x 2.1m | 2.0m x 2.6m
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1400
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 608.496 | 941.72
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 286.29
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 213 | 230 | 266 | 283 | 348 | 408 | 462 | 506 | 584 | 656
5 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 |  | Total | #REF! | 560.62 | 596.62 | 698.64 | 829.75 | 960.6 | 1090.18 | 1214.47 | 1377.48 | 1884.01
BWSC pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 1.0m x 1.4m |  |  | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.2m | 1.8m x 2.3m
| Pipe dia in mm = |  | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100mm | 1200mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 426 | 476 | 596 | 733 | 854 | 971 | 1142 | 1262 | 1483 | 1660
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 636.62 | 690.62 | 756.62 | 806.62 | 1011.64 | 1214.75 | 1406.6 | 1599.18 | 1850.47 | 2026.5 | 2375.58 | 4820.73
GRP pipes - Earth work
5 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for GRP pipes with 300 mm thick sand encasing and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.95 x 1.55 | 1.0 x 1.6 | 1.05 x 1.65 | 1.1 x 1.7 | 1.2 x 1.8 | 1.3 x 1.9 | 1.4 x 2.0 | 1.5 x 2.1 | 1.6 x 2.2 | 1.6 x 2.2
| Pipe dia in mm = |  | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000 | 1000
1 | Earth work |  | 266.6697 | 289.76 | 313.7557 | 338.657 | 391.176 | 447.317 | 507.08 | 570.465 | 637.472 | #VALUE!
2 | Extra allowance |  | 81.07 | 88.09 | 95.38 | 102.95 | 118.92 | 135.99 | 154.15 | 173.42 | 193.79 | 0
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE!
5 | Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. |  | 160 | 240 | 293 | 373 | 399 | 452 | 532 | 585 | 679 | 679
6 | Add MA |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE!
6 | AC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for AC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7 | 1.3x1.8 | 1.4x2.0 | 1.4x2.0 | 1.5x2.1 | 1.5x2.1 | 1.6x2.3
| Pipe dia in mm = |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 850 | 900 | 1000
1 | Earth work |  | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 507.08 | 507.08 | 570.465 | 570.465 | 666.448
2 | Extra allowance |  | 59.46 | 59.46 | 59.46 | 59.46 | 64.41 | 64.41 | 64.41 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31 | 128.83 | 154.15 | 154.15 | 173.42 | 173.42 | 202.6
3 | Sand cushion cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | sub-total | 255.048 | 255.048 | 255.048 | 255.048 | 276.297 | 276.297 | 276.297 | 330.62 | 330.62 | 357.7164 | 415.636 | 481.754 | 552.604 | 661.23 | 661.23 | 743.885 | 743.885 | 869.048
5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing.
|  |  | 35 | 52 | 57 | 68 | 89 | 107 | 132 | 224 | 336 | 409 | 520 | 559 | 624 | 694 | 730 | 779 | 850 | 875
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 290.048 | 307.048 | 312.048 | 323.048 | 365.297 | 383.297 | 408.297 | 554.62 | 666.62 | 766.7164 | 935.636 | 1040.754 | 1176.604 | 1355.23 | 1391.23 | 1522.885 | 1593.885 | 1744.048
RCC pipes - Earth work
Earth work excavation in all soils upto SDR except hard rock requiring blasting for RCC pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  | 0.9 x 1.2 |  |  |  | 0.9 x 1.3 |  |  | 1.0 x 1.4 |  |  | 1.1 x 1.6 | 1.2 x 1.7
|  |  | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| 1 | Earth work | 195.588 | 195.588 | 195.588 | 195.588 | 211.887 | 211.887 | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444
| 2 | Extra allowance | 59.46 | 59.46 | 21.66 | 59.46 | 64.41 | 64.41 | 21.66 | 77.08 | 77.08 | 104.1764 | 96.9 | 112.31
| 3 | Sand cushion cost | 0 | 0 | 0 | 0 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
| 4 | Refilling charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Lowering, Laying, jointing, testing HFT pressure including cost of ruuber rings, cost of transportation of water and emptying pipe line after completion of field testing. | 46.29 | 57.59 |  | 73.04 | 86.97 | 113.65 | 120.12 | 134.48 | 149.17 | 164.84 | 191.15 | 224.18 | 292 | 350 | 420 | 503
| 6 | Add MA | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PCCP pipes - Earth work
4 | Earth work excavation in all soils upto SDR except hard rock requiring blasting for BWSCP pipes and filling with excavated soils including laying jointing testing of pipe line but excluding cost of materials etc. complete
| Trench size |  |  |  | 1.0m x 1.4m | 1.0mx1.40m | 1.1m x 1.6m | 1.2m x 1.7m | 1.3mx 1.8m | 1.4m x 1.9m | 1.5mx 2.0m | 1.6mx 2.1m | 1.7m x 2.3m | 1.8m x 2.4m | 1.9x2.5 | 2.0x2.6 | 2.1x2.7 | 2.2x2.8 | 2.3x2.9 | 2.4x3.0 | 2.5x3.1 | 2.6x3.2
| Pipe dia in mm = |  | 300 | 350 | 400mm | 450mm | 500 mm | 600mm | 700mm | 800mm | 900mm | 1000mm | 1100mm | 1200mm | 1300mm | 1400mm | 1500mm | 1600mm | 1700mm | 1800mm | 1900mm | 2000mm
1 | Earth work |  | 253.54 | 253.54 | 253.54 | 253.54 | 318.736 | 369.444 | 423.774 | 481.726 | 543.3 | 579.52 | 677.314 | 782.352 | 860.225 | 941.72 | 1026.837 | 1115.576 | 1207.937 | 1303.92 | 1403.525 | 1506.752
2 | Extra allowance |  | 77.08 | 77.08 | 77.08 | 77.08 | 96.9 | 112.31 | 128.83 | 146.45 | 165.17 | 184.98 | 215.27 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38 | 2378.38
3 | Refilling charges |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laying, jointing, testing HFT pressure including cost of site welding and fixing of Diapher cloth, cost of transportation of water and emptying pipe line after completion of field testing. |  | 306 | 360 | 449 | 528 | 575 | 673 | 767 | 880 | 992 | 1087 | 1232 | 1344 | 1439 | 1584 | 1758 | 1903 | 2143 | 2272 | 2478 | 2638
|  | Add MA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 636.62 | 690.62 | 779.62 | 858.62 | 990.64 | 1154.75 | 1319.6 | 1508.18 | 1700.47 | 1851.5 | 2124.58 | 4504.73 | 4677.61 | 4904.1 | 5163.22 | 5396.96 | 5729.32 | 5954.3 | 6259.91 | 6523.13
Note on J7: to be changed based on the corresponding lead from master copy

## PH Data EW
Index-code | S. No |  | Description | Unit | Quantity | Rate Rs. | Amount Rs. | Remarks
| 1 |  | 2 | 3 | 4 | 5 | 6 | 7
RBR-FNDN-1 | 1 |  | Excavation for Structures
Earthwork in excavation for structures as per drawing and technical specifications Clause 305.1 including setting out, construction of shoring and bracing, removal of stumps and other deleterious material and disposal upto a lead of 50 m, dressing of sides and bottom and backfilling in trenches with excavated suitable material as per Technical Specification 305 MORD / 304 MORTH
Note : Classifications of Earth Work Specification are as per 302.2.1(a) of MORD and 301.2.1 of MORT&H
|  | (I) | Ordinary soil
|  | (A) | Manual Means
|  | (i) | Upto 3 m depth
Unit = cum
Taking output = 10 cum
a) Labour
|  |  | Mate | day | -
|  |  | Mazdoor (Unskilled) | day | 3.64 | 605 | 2202.2 | P NO 41 | SSR 25-26 |  | 350 | 127.4
b&c) Overheads & Contractors Profit
Cost for 10 cum = a+b+c
|  |  | Rate per cum = (a+b+c)/10 |  |  |  | 220.22
Note : 1. Cost of dewatering may be added, where required, up to 5 per cent of labour cost. Assessment for dewatering shall be made as per site conditions.
|  |  | 2. The cost of shoring and shuttering, where needed, may be added on cost of excavation for open foundation. |  | 0.01
3. The excavated earth if found suitable, can be used partly for backfilling in trenches & partly for road work. Hence cost of disposal has not been added except for marshy soil. This note is common to all cases of item 11.1 excluding 11.1 V
|  | (B) | Mechanical Means
|  | i | Upto 3 m depth
Unit = cum
Taking output = 240 cum
a) Labour
|  |  | Mate | day | -
|  |  | Mazdoor (Unskilled) | day | 8.32 | 605 | 5033.6 | P NO 41 | SSR 25-26 |  | 350 | 2912
b) Machinery
|  |  | Hydraulic Excavator 1 cum bucket capacity | hour | 6 | 3275.2 | 19651.2 | SSR 24-25 | Pg. NO 46 | SHOVEL 0.85 cum 110 hp | 2821.5 | 16929 | NO CREWCHARGES
|  |  | c&d) Overheads & Contractors Profit | [5 empty] | Sl. No. 52 |  |  | 19841
|  |  | Cost for 240 cum = a+b+c+d |  |  |  | 24684.8 |  |  |  |  | 82.6708
|  |  | Rate per cum = (a+b+c+d)/240 |  |  |  | 102.8533

## Road Cutting
DATA Sheet for Road Cutting
|  | CC road cutting | B.T road cutting
|  | Pg. No. 611 | Pg. No.611
|  | 2392 | 1150
| Add 13.615% | 325.6708 | 156.5725
| Total:: | 2717.6708 | 1306.5725

## lowering
Statement Showing Comparative Data (2017-18)
Drinking Water Supply Schemes (Public Health)
Index-code | S No | Description | Unit | Quantity | Rate Rs. | Amt Rs. | Remarks
| 1 | 2 | 3 | 4 | 5 | 6 | 7
Sub Analysis
Common Data |  | Lowering C.I. Pipes, A class and specials with s/s ends carefully into trench and laying them true to alignment and gradient including all sundries but excluding cost and conveyance of pipes from source of supply. (Reference to specifications. BIS No.3114/94) | [7 empty] | CI LA, A lowering s/s
Assumtion 10 m
200 mm dia CI pipes 5m long (class ‘A’)
Weight = 2 x 257 kgs = 514 kgs = 5.14 quintal
(a) LABOUR:
|  | Plumber 1st class | day | 0.102 | 540 | 55.08
|  | Plumber 2nd class | day | 0.238 | 425 | 101.15
|  | Man mazdoor | day | 1.33 | 400 | 532
|  | (b) Cost for 10 metres |  |  |  | 688.23
|  | Rate per metre = b/10 |  |  |  | 68.82
|  | Rate for 1 kg = b/514 |  |  |  | 1.34
PHE-LCIS-1 | 1 | Lowering C.I. / D.I. Pipes (all classes) and specials (fittings) with s/s ends carefully into trenches and laying them true to alignment and gradient including all sundries but excluding cost and conveyance of pipes from source of supply (Ref to specifications. BIS No.3114/1994) | [7 empty] | CI/DI S/S LOWERING
Note : The Labour charges for cost of Lowering & Laying per 1 kg weight shall be as per sub-analysis made for 200 mm dia CI Pipes S/s ends.
Details of cost for 5m
| i | 80 mm dia pipe
Weight of 5m length = (79 +85.5 + 92)/3 = 85.5 kgs
|  | (a) Labour charges for laying | kgs | 85.5 | 1.34 | 114.57
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 114.57
|  | Rate per metre = c/5 |  |  |  | 22.91
| ii | 100 mm dia pipe
Weight of 5m length = (100+109+117)/3 = 108.67 kgs
|  | (a) Labour charges for laying | kgs | 108.67 | 1.34 | 145.61
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 145.61
|  | Rate per metre = c/5 |  |  |  | 29.12
| iii | 125 mm dia pipe
Weight of 5m length = (130+141+153)/3 = 141.33 kgs
|  | (a) Labour charges for laying | kgs | 141.33 | 1.34 | 189.38
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 189.38
|  | Rate per metre = c/5 |  |  |  | 37.88
| iv | 150mm dia pipe
Weight of 5m length = (162+178+191)/3 = 177 kgs
|  | (a) Labour charges for laying | kgs | 177 | 1.34 | 237.18
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 237.18
|  | Rate per metre = c/5 |  |  |  | 47.44
| v | 200 mm dia pipe
Weight of 5m length = (237+257+278)/3 = 257.33 kgs
|  | (a) Labour charges for laying | kgs | 257.33 | 1.34 | 344.82
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 344.82
|  | Rate per metre = c/5 |  |  |  | 68.96
| vi | 250 mm dia pipe
Weight of 5m length = (319+348+376)/3 = 347.67 kgs
|  | (a) Labour charges for laying | kgs | 347.67 | 1.34 | 465.87
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 465.87
|  | Rate per metre = c/5 |  |  |  | 93.17
| vii | 300 mm dia pipe
Weight of 5m length = (412+450+487)/3 = 449.67 kgs
|  | (a) Labour charges for laying | kgs | 449.67 | 1.34 | 602.55
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 602.55
|  | Rate per metre = c/5 |  |  |  | 120.51
| viii | 350 mm dia pipe
Weight of 5m length =(519+563+610)/3=564
|  | (a) Labour charges for laying | kgs | 564 | 1.34 | 755.76
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 755.76
|  | Rate per metre = c/5 |  |  |  | 151.15
| ix | 400 mm dia pipe
Weight of 5m length =(631+690+744)/3=688.33
|  | (a) Labour charges for laying | kgs | 688.33 | 1.34 | 922.36
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 922.36
|  | Rate per metre = c/5 |  |  |  | 184.47
| x | 450mm dia pipe s/s for 5m
Weight of 5m length =(761+836+901)/3=832.67
|  | (a) Labour charges for laying | kgs | 832.67 | 1.34 | 1115.77
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 1115.77
|  | Rate per metre = c/5 |  |  |  | 223.15
| xi | 500 mm dia pipe
Weight of 5m length =(892+971+1049)/3=970.67
|  | (a) Labour charges for laying | kgs | 970.67 | 1.34 | 1300.69
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 1300.69
|  | Rate per metre = c/5 |  |  |  | 260.14
| xii | 600 mm dia pipe
Weight of 5m length =(1188+1296+1404)/3=1296
|  | (a) Labour charges for laying | kgs | 1296 | 1.34 | 1736.64
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 1736.64
|  | Rate per metre = c/5 |  |  |  | 347.33
| xiii | 700mm dia pipe s/s for 5m
Weight of 5m length =(1533+1675+1808)/3=1672
|  | (a) Labour charges for laying | kgs | 1672 | 1.34 | 2240.48
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 2240.48
|  | Rate per metre = c/5 |  |  |  | 448.1
| xiv | 750 mm dia pipe
Weight of 5m length =(1718+1876+2029)/3=1874.33
|  | (a) Labour charges for laying | kgs | 1874.33 | 1.34 | 2511.6
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 2511.6
|  | Rate per metre = c/5 |  |  |  | 502.32
| xv | 800 mm dia pipe
Weight of 5m length =(1922+2093+2263)/3=2092.67
|  | (a) Labour charges for laying | kgs | 2092.67 | 1.34 | 2804.17
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 2804.17
|  | Rate per metre = c/5 |  |  |  | 560.83
| xvi | 900 mm dia pipe
Weight of 5m length =(2342+2544+2766)/3=2554
|  | (a) Labour charges for laying | kgs | 2544 | 1.34 | 3408.96
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 3408.96
|  | Rate per metre = c/5 |  |  |  | 681.79
| xvii | 1000 mm dia pipe
Weight of 5m length =(2814+3072+3318)/3=3068
|  | (a) Labour charges for laying | kgs | 3068 | 1.34 | 4111.12
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 4111.12
|  | Rate per metre = c/5 |  |  |  | 822.22
| xvii | 1100 mm dia pipe | [5 empty] | Weight of pipes to be corrected
Weight of 5m length =(2814+3072+3318)/3=3068
|  | (a) Labour charges for laying | kgs | 3068 | 1.34 | 4111.12
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | (c) Cost for 5 metres = a+b |  |  |  | 4111.12
|  | Rate per metre = c/5 |  |  |  | 822.22
PHE-LCIF-2 | 2 | Lowering C.I. / D.I. Pipes (all classes) and specials (fittings) with flanged ends carefully into trench and laying them true to alignment and gradient including all sundries but excluding cost and conveyance of pipes from source of supply. (Reference to specifications. BIS No.3114/1994) | [7 empty] | CI/DI FLANGED LOWERING
Note : The cost of lowering and laying is taken as per sub analysis made for S/S ends.
Details of cost for 10m
| i | 80 mm dia pipe
Weight of 1m length = 19.8+(2x3.7)/2.75 = 22.49 kgs
|  | (a) Labour charges for laying | kgs | 22.49 | 1.34 | 30.13
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 30.13
| ii | 100 mm dia pipe
Weight of 1m length = 25.4+(2x4.2)/2.75 = 28.45 kgs
|  | (a) Labour charges for laying | kgs | 28.45 | 1.34 | 38.12
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 38.12
| iii | 125 mm dia pipe
Weight of 1m length = 33.1+(2x5.3)/2.75 = 36.95 kgs
|  | (a) Labour charges for laying | kgs | 36.95 | 1.34 | 49.51
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 49.51
| iv | 150mm dia pipe
Weight of 1m length = 41.6+(2x6.7)/2.75 = 46.47 kgs
|  | (a) Labour charges for laying | kgs | 46.47 | 1.34 | 62.26
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 62.26
| v | 200 mm dia pipe
Weight of 1m length = 60.1+(2x9.3)/2.75 = 66.86 kgs
|  | (a) Labour charges for laying | kgs | 66.86 | 1.34 | 89.59
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 89.59
| vi | 250 mm dia pipe
Weight of 1m length = 81.8+(2x12)/2.75 = 90.53 kgs
|  | (a) Labour charges for laying | kgs | 90.53 | 1.34 | 121.31
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 121.31
| vii | 300 mm dia pipe
Weight of 1m length = 106.1+(2x14.8)/2.75 = 116.86 kgs
|  | (a) Labour charges for laying | kgs | 116.86 | 1.34 | 156.59
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 156.59
| viii | 350 mm dia pipe
Weight of 1m length = 133.5+(2x19)/2.75 = 147.32 kgs
|  | (a) Labour charges for laying | kgs | 147.32 | 1.34 | 197.4
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 197.4
| ix | 400 mm dia pipe
Weight of 1m length = 162.6+(2x23.4)/2.75 = 179.62 kgs
|  | (a) Labour charges for laying | kgs | 179.62 | 1.34 | 240.69
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 240.69
| x | 450mm dia pipe
Weight of 1m length = 197+(2x26.5)/2.75 = 216.27 kgs
|  | (a) Labour charges for laying | kgs | 216.27 | 1.34 | 289.8
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 289.8
| xi | 500 mm dia pipe
Weight of 1m length = 229.3+(2x32.1)/2.75 = 252.65 kgs
|  | (a) Labour charges for laying | kgs | 252.65 | 1.34 | 338.55
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 338.55
| xii | 600 mm dia pipe
Weight of 1m length = 306.5+(2x44)/2.75 = 338.5 kgs
|  | (a) Labour charges for laying | kgs | 338.5 | 1.34 | 453.59
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 453.59
| xiii | 700mm dia pipe s/s for 5m
Weight of 1m length = 394.3+(2x59.9)/2.75 = 437.86 kgs
|  | (a) Labour charges for laying | kgs | 437.86 | 1.34 | 586.73
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 586.73
| xiv | 750 mm dia pipe
Weight of 1m length = 443.8+(2x59.7)/2.75 = 494.49 kgs
|  | (a) Labour charges for laying | kgs | 494.49 | 1.34 | 662.61
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 662.61
PHE-LCIF-2A | 2 A | Sub Analysis : (Basic Data)
|  | OBSERVED DATA FOR TESTING OF 450 MM DIA PSC MAIN : Pumping main to Hydralic field test pressure including transportation of Water with minimum lead of 500 M | [7 empty] | TESTING
(Length = 500 Mts) taking out put / 500 Mts. Unit = 1 Rmt.
Labour
Fitters (2 x 3 days)
|  | Fitters I Class | day | 3 | 775 | 2325 |  | P-41
|  | Fitters II Class | day | 3 | 650 | 1950 |  | P-42
Machinery
|  | Hire chargers for Hydralic field test pressure testing including transportation of water @ Rs. 1200/- (1000+200) / day | days | 3 | 1200 | 3600 | To be confirmed |  | 0.15896
|  | Materials | [6 empty] | 79.4813
|  | Pressure guage | Nos | 0.05 | 0 | 0 | LR |  | 626
|  | 3/4" G.I. Pipe (20 mm), Pg.No. 222 | RM | 3 | 241 | 723 |  | P-318 | 6160
|  | Specials | Ls |  |  | 7.23 |  |  | 2551.2
|  | Dummies | No. | 0.1 | 0 | 0 | LR
|  | Diesel (2 Lts. / Hr) 30 Hrs. | Lts. | 60 | 95.7 | 5742 |  | P-35
|  | (T) Total Rate per 500 Mts. |  |  |  | 14347.23
|  | (r) Rate per 1 Rmt for 450 mm dia |  |  |  | 28.69
|  | (R) Rate per 1 Rmt for 10 mm dia = (10/450) x r |  |  |  | 0.63756
Note : Proportionate Testing Charges may be arrived, keeping the diametre of pipe based on this analysis, for an varities of pipes for various Dia Pipes.
PHE-JCIS-3 | 3 | Jointing CI /DI pipes & fittings with s/s ends including cost of pig lead, hemp yarn and sundries such as cost of fuel for melting lead, filling with water with lead up to 500m and testing to required pressure complete. (Reference to specifications. BIS No.3114/94/12288:1997) | [7 empty] | CI/DI S/S PIG IRON JOINTING
Details of cost for 10 joints
| i | 80 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.135 | 515 | 69.52
|  | Plumber 2nd class | day | 0.32 | 400 | 128
|  | Man mazdoor | day | 1.2 | 350 | 420
b) Material
|  | Fuel wood | q | 0.19 | 550 | 104.5
|  | Kerosene | litre | 0.33 | 33 | 10.89
|  | Spun yarn | kg | 1 | 134 | 134
|  | Pig lead | kg | 20 | 335 | 6700
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 5.1 | 255
|  | (d) Total = a+b+c |  |  |  | 7821.91
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 8.73 |  | 872.52
|  | (f) Total = d+e |  |  |  | 7830.64
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 7830.64
|  | Rate per joint =h/10 |  |  |  | 783.06
| ii | 100 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.22 | 515 | 113.3
|  | Plumber 2nd class | day | 0.53 | 400 | 212
|  | Man mazdoor | day | 1.5 | 350 | 525
b) Material
|  | Fuel wood | q | 0.25 | 550 | 137.5
|  | Kerosene | litre | 0.33 | 33 | 10.89
|  | Spun yarn | kg | 1.8 | 134 | 241.2
|  | Pig lead | kg | 24 | 335 | 8040
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 6.3756 | 318.77
|  | (d) Total = a+b+c |  |  |  | 9598.66
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 11.69 |  | 1169.07
|  | (f) Total = d+e |  |  |  | 9610.35
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 9610.35
|  | Rate per joint =h/10 |  |  |  | 961.04
| iii | 125 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.22 | 515 | 113.3
|  | Plumber 2nd class | day | 0.53 | 400 | 212
|  | Man mazdoor | day | 1.5 | 350 | 525
b) Material
|  | Fuel wood | q | 0.37 | 550 | 203.5
|  | Kerosene | litre | 0.7 | 33 | 23.1
|  | Spun yarn | kg | 2 | 134 | 268
|  | Pig lead | kg | 28 | 335 | 9380
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 7.9694 | 398.47
|  | (d) Total = a+b+c |  |  |  | 11123.37
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 12.49 |  | 1248.77
|  | (f) Total = d+e |  |  |  | 11135.86
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 11135.86
|  | Rate per joint =h/10 |  |  |  | 1113.59
| iv | 150 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.27 | 515 | 139.05
|  | Plumber 2nd class | day | 0.63 | 400 | 252
|  | Man mazdoor | day | 1.65 | 350 | 577.5
b) Material
|  | Fuel wood | q | 0.42 | 550 | 231
|  | Kerosene | litre | 0.76 | 33 | 25.08
|  | Spun yarn | kg | 2 | 134 | 268
|  | Pig lead | kg | 36 | 335 | 12060
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 9.5633 | 478.16
|  | (d) Total = a+b+c |  |  |  | 14030.79
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 14.47 |  | 1446.71
|  | (f) Total = d+e |  |  |  | 14045.26
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 14045.26
|  | Rate per joint =h/10 |  |  |  | 1404.53
| v | 200 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.27 | 515 | 139.05
|  | Plumber 2nd class | day | 0.63 | 400 | 252
|  | Man mazdoor | day | 1.65 | 350 | 577.5
b) Material
|  | Fuel wood | q | 0.56 | 550 | 308
|  | Kerosene | litre | 0.756 | 33 | 24.94
|  | Spun yarn | kg | 3 | 134 | 402
|  | Pig lead | kg | 54 | 335 | 18090
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 12.7511 | 637.55
|  | (d) Total = a+b+c |  |  |  | 20431.04
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 16.06 |  | 1606.1
|  | (f) Total = d+e |  |  |  | 20447.1
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 20447.1
|  | Rate per joint =h/10 |  |  |  | 2044.71
| vi | 250 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.28 | 515 | 144.2
|  | Plumber 2nd class | day | 0.65 | 400 | 260
|  | Man mazdoor | day | 1.8 | 350 | 630
b) Material
|  | Fuel wood | q | 0.65 | 550 | 357.5
|  | Kerosene | litre | 1.14 | 33 | 37.62
|  | Spun yarn | kg | 3.5 | 134 | 469
|  | Pig lead | kg | 66 | 335 | 22110
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 15.9389 | 796.94
|  | (d) Total = a+b+c |  |  |  | 24805.26
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 18.31 |  | 1831.14
|  | (f) Total = d+e |  |  |  | 24823.57
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 24823.57
|  | Rate per joint =h/10 |  |  |  | 2482.36
| vii | 300 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.36 | 515 | 185.4
|  | Plumber 2nd class | day | 0.84 | 400 | 336
|  | Man mazdoor | day | 1.8 | 350 | 630
b) Material
|  | Fuel wood | q | 0.75 | 550 | 412.5
|  | Kerosene | litre | 1.52 | 33 | 50.16
|  | Spun yarn | kg | 4.8 | 134 | 643.2
|  | Pig lead | kg | 76 | 335 | 25460
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 19.1267 | 956.33
|  | (d) Total = a+b+c |  |  |  | 28673.59
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 21.08 |  | 2107.73
|  | (f) Total = d+e |  |  |  | 28694.67
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 28694.67
|  | Rate per joint =h/10 |  |  |  | 2869.47
| viii | 350 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.4 | 515 | 206
|  | Plumber 2nd class | day | 0.95 | 400 | 380
|  | Man mazdoor | day | 2.25 | 350 | 787.5
b) Material
|  | Fuel wood | q | 0.93 | 550 | 511.5
|  | Kerosene | litre | 1.7 | 33 | 56.1
|  | Spun yarn | kg | 6 | 134 | 804
|  | Pig lead | kg | 90 | 335 | 30150
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 22.3144 | 1115.72
|  | (d) Total = a+b+c |  |  |  | 34010.82
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 24.89 |  | 2489.22
|  | (f) Total = d+e |  |  |  | 34035.71
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 34035.71
|  | Rate per joint =h/10 |  |  |  | 3403.57
| ix | 400 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.31 | 515 | 159.65
|  | Plumber 2nd class | day | 0.74 | 400 | 296
|  | Man mazdoor | day | 2.25 | 350 | 787.5
b) Material
|  | Fuel wood | q | 1.12 | 550 | 616
|  | Kerosene | litre | 1.7 | 33 | 56.1
|  | Spun yarn | kg | 7.5 | 134 | 1005
|  | Pig lead | kg | 105 | 335 | 35175
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 25.5022 | 1275.11
|  | (d) Total = a+b+c |  |  |  | 39370.36
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 25.18 |  | 2518.26
|  | (f) Total = d+e |  |  |  | 39395.54
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 39395.54
|  | Rate per joint =h/10 |  |  |  | 3939.55
| x | 450 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.54 | 515 | 278.1
|  | Plumber 2nd class | day | 1.26 | 400 | 504
|  | Man mazdoor | day | 2.55 | 350 | 892.5
b) Material
|  | Fuel wood | q | 1.21 | 550 | 665.5
|  | Kerosene | litre | 2.27 | 33 | 74.91
|  | Spun yarn | kg | 9.5 | 134 | 1273
|  | Pig lead | kg | 150 | 335 | 50250
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 28.69 | 1434.5
|  | (d) Total = a+b+c |  |  |  | 55372.51
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 31.09 |  | 3109.1
|  | (f) Total = d+e |  |  |  | 55403.6
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 55403.6
|  | Rate per joint =h/10 |  |  |  | 5540.36
| xi | 500 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.58 | 515 | 298.7
|  | Plumber 2nd class | day | 1.37 | 400 | 548
|  | Man mazdoor | day | 2.7 | 350 | 945
b) Material
|  | Fuel wood | q | 1.31 | 550 | 720.5
|  | Kerosene | litre | 2.27 | 33 | 74.91
|  | Spun yarn | kg | 10 | 134 | 1340
|  | Pig lead | kg | 160 | 335 | 53600
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 31.8778 | 1593.88
|  | (d) Total = a+b+c |  |  |  | 59120.99
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 33.86 |  | 3385.58
|  | (f) Total = d+e |  |  |  | 59154.85
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 59154.85
|  | Rate per joint =h/10 |  |  |  | 5915.49
| xii | 600 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.68 | 515 | 350.2
|  | Plumber 2nd class | day | 1.57 | 400 | 628
|  | Man mazdoor | day | 3 | 350 | 1050
b) Material
|  | Fuel wood | q | 1.68 | 550 | 924
|  | Kerosene | litre | 2.54 | 33 | 83.82
|  | Spun yarn | kg | 12 | 134 | 1608
|  | Pig lead | kg | 205 | 335 | 68675
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 38.2533 | 1912.66
|  | (d) Total = a+b+c |  |  |  | 75231.68
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 39.41 |  | 3940.86
|  | (f) Total = d+e |  |  |  | 75271.09
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 75271.09
|  | Rate per joint =h/10 |  |  |  | 7527.11
| xiii | 700 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.77 | 515 | 396.55
|  | Plumber 2nd class | day | 1.78 | 400 | 712
|  | Man mazdoor | day | 3.3 | 350 | 1155
b) Material
|  | Fuel wood | q | 2.1 | 550 | 1155
|  | Kerosene | litre | 3.2 | 33 | 105.6
|  | Spun yarn | kg | 13.5 | 134 | 1809
|  | Pig lead | kg | 240 | 335 | 80400
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 44.6289 | 2231.44
|  | (d) Total = a+b+c |  |  |  | 87964.59
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 44.95 |  | 4494.99
|  | (f) Total = d+e |  |  |  | 88009.54
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 88009.54
|  | Rate per joint =h/10 |  |  |  | 8800.95
| xiv | 750 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.77 | 515 | 396.55
|  | Plumber 2nd class | day | 1.78 | 400 | 712
|  | Man mazdoor | day | 3.3 | 350 | 1155
b) Material
|  | Fuel wood | q | 2.4 | 550 | 1320
|  | Kerosene | litre | 3.5 | 33 | 115.5
|  | Spun yarn | kg | 14.5 | 134 | 1943
|  | Pig lead | kg | 270 | 335 | 90450
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 47.8167 | 2390.83
|  | (d) Total = a+b+c |  |  |  | 98482.88
|  | (e) Add for water charges @ 1%on Labour & Testing Charges |  |  |  | 46.54 |  | 4654.38
|  | (f) Total = d+e |  |  |  | 98529.42
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 98529.42
|  | Rate per joint =h/10 |  |  |  | 9852.94
| xv | 800 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.77 | 515 | 396.55
|  | Plumber 2nd class | day | 1.78 | 400 | 712
|  | Man mazdoor | day | 3.3 | 350 | 1155
b) Material
|  | Fuel wood | q | 2.33 | 550 | 1281.5
|  | Kerosene | litre | 3.41 | 33 | 112.53
|  | Spun yarn | kg | 15.3 | 134 | 2050.2
|  | Pig lead | kg | 325 | 335 | 108875
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment and Labour, Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 51.0044 | 2550.22
|  | (d) Total = a+b+c |  |  |  | 117133
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 48.14 |  | 4813.77
|  | (f) Total = d+e |  |  |  | 117181.14
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 117181.14
|  | Rate per joint =h/10 |  |  |  | 11718.11
PHE-JCIR-4 | 4 | Jointing C.I., D.I. pipes and fittings with rubber gasket (push-on-joint), excluding the cost of the gasket but including all sundries filling with water, with a water lead up to 500m and testing to required pressure, etc. complete Reference to specifications IS 3114/1994/12888/1987 | [7 empty] | CI/DI S/S RUBBER GASKET JOINTING
Note : Rubber Gaskets shall be added seperately.
Details of cost for 10 Joints
| i | 80 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.3 | 400 | 120
|  | Man mazdoor | day | 0.8 | 350 | 280
b) Material
|  | Rubber gasket | each | 10 | 63 | 630
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 5.1004 | 255.02
|  | (d) Total = a+b+c |  |  |  | 1285.02
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 6.55 |  | 655.02
|  | (f) Total = d+e+f |  |  |  | 1291.57
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 1291.57
|  | Rate per joint = h/10 |  |  |  | 129.16 |  | 12.916 | 25.832
| ii | 100 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.3 | 400 | 120
|  | Man mazdoor | day | 0.8 | 350 | 280
b) Material
|  | Rubber gasket | each | 10 | 98 | 980
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 6.3756 | 318.78
|  | (d) Total = a+b+c |  |  |  | 1698.78
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 7.19 |  | 718.78
|  | (f) Total = d+e+f |  |  |  | 1705.97
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 1705.97
|  | Rate per joint = h/10 |  |  |  | 170.6
| iii | 125 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.5 | 400 | 200
|  | Man mazdoor | day | 1 | 350 | 350
b) Material
|  | Rubber gasket | each | 10 | 117 | 1170
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 7.9694 | 398.47
|  | (d) Total = a+b+c |  |  |  | 2118.47
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 9.48 |  | 948.47
|  | (f) Total = d+e+f |  |  |  | 2127.95
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 2127.95
|  | Rate per joint = h/10 |  |  |  | 212.8
| iv | 150 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.6 | 400 | 240
|  | Man mazdoor | day | 1.1 | 350 | 385
b) Material
|  | Rubber gasket | each | 10 | 143 | 1430
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 9.5633 | 478.17
|  | (d) Total = a+b+c |  |  |  | 2533.17
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 11.03 |  | 1103.17
|  | (f) Total = d+e+f |  |  |  | 2544.2
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 2544.2
|  | Rate per joint = h/10 |  |  |  | 254.42
| v | 200 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.6 | 400 | 240
|  | Man mazdoor | day | 1.1 | 350 | 385
b) Material
|  | Rubber gasket | each | 10 | 174 | 1740
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 12.7511 | 637.56
|  | (d) Total = a+b+c |  |  |  | 3002.56
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 12.63 |  | 1262.56
|  | (f) Total = d+e+f |  |  |  | 3015.19
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 3015.19
|  | Rate per joint = h/10 |  |  |  | 301.52
| vi | 250 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.62 | 400 | 248
|  | Man mazdoor | day | 1.2 | 350 | 420
b) Material
|  | Rubber gasket | each | 10 | 194 | 1940
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 15.9389 | 796.94
|  | (d) Total = a+b+c |  |  |  | 3404.94
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 14.65 |  | 1464.94
|  | (f) Total = d+e+f |  |  |  | 3419.59
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 3419.59
|  | Rate per joint = h/10 |  |  |  | 341.96
| vii | 300 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.8 | 400 | 320
|  | Man mazdoor | day | 1.2 | 350 | 420
b) Material
|  | Rubber gasket | each | 10 | 295 | 2950
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 19.1267 | 956.33
|  | (d) Total = a+b+c |  |  |  | 4646.33
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 16.96 |  | 1696.33
|  | (f) Total = d+e+f |  |  |  | 4663.29
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 4663.29
|  | Rate per joint = h/10 |  |  |  | 466.33
| viii | 350 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 0.9 | 400 | 360
|  | Man mazdoor | day | 1.5 | 350 | 525
b) Material
|  | Rubber gasket | each | 10 | 374 | 3740
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 22.3144 | 1115.72
|  | (d) Total = a+b+c |  |  |  | 5740.72
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 20.01 |  | 2000.72
|  | (f) Total = d+e+f |  |  |  | 5760.73
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 5760.73
|  | Rate per joint = h/10 |  |  |  | 576.07
| viii | 400 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1 | 400 | 400
|  | Man mazdoor | day | 1.5 | 350 | 525
b) Material
|  | Rubber gasket | each | 10 | 408 | 4080
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 25.5022 | 1275.11
|  | (d) Total = a+b+c |  |  |  | 6280.11
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 22 |  | 2200.11
|  | (f) Total = d+e+f |  |  |  | 6302.11
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 6302.11
|  | Rate per joint = h/10 |  |  |  | 630.21
| ix | 450 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.2 | 515 | 618
|  | Man mazdoor | day | 1.7 | 400 | 680
b) Material
|  | Rubber gasket | each | 10 | 439 | 4390
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 28.69 | 1434.5
|  | (d) Total = a+b+c |  |  |  | 7122.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 27.33 |  | 2732.5
|  | (f) Total = d+e+f |  |  |  | 7149.83
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 7149.83
|  | Rate per joint = h/10 |  |  |  | 714.98
| x | 500 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.3 | 400 | 520
|  | Man mazdoor | day | 1.8 | 350 | 630
b) Material
|  | Rubber gasket | each | 10 | 609 | 6090
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 31.8778 | 1593.89
|  | (d) Total = a+b+c |  |  |  | 8833.89
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 27.44 |  | 2743.89
|  | (f) Total = d+e+f |  |  |  | 8861.33
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 8861.33
|  | Rate per joint = h/10 |  |  |  | 886.13
| xi | 600 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.5 | 400 | 600
|  | Man mazdoor | day | 2 | 350 | 700
b) Material
|  | Rubber gasket | each | 10 | 722 | 7220
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 38.2533 | 1912.67
|  | (d) Total = a+b+c |  |  |  | 10432.67
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 32.13 |  | 3212.67
|  | (f) Total = d+e+f |  |  |  | 10464.8
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 10464.8
|  | Rate per joint = h/10 |  |  |  | 1046.48
| xii | 650 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.6 | 400 | 640
|  | Man mazdoor | day | 2.1 | 350 | 735
b) Material
|  | Rubber gasket | each | 10 | 840.5 | 8405
|  | c) Testing |  |  | average rate
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 41.4411 | 2072.06
|  | (d) Total = a+b+c |  |  |  | 11852.06
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 34.47 |  | 3447.06
|  | (f) Total = d+e+f |  |  |  | 11886.53
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 11886.53
|  | Rate per joint = h/10 |  |  |  | 1188.65
| xiii | 700 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.7 | 400 | 680
|  | Man mazdoor | day | 2.2 | 350 | 770
b) Material
|  | Rubber gasket | each | 10 | 959 | 9590
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 44.6289 | 2231.44
|  | (d) Total = a+b+c |  |  |  | 13271.44
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 36.81 |  | 3681.44
|  | (f) Total = d+e+f |  |  |  | 13308.25
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 13308.25
|  | Rate per joint = h/10 |  |  |  | 1330.83
| xix | 750 mm dia pipe
a) Labour
|  | Plumber 2nd class | day | 1.7 | 400 | 680
|  | Man mazdoor | day | 2.2 | 350 | 770
b) Material
|  | Rubber gasket | each | 10 | 1065 | 10650
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 47.8167 | 2390.83
|  | (d) Total = a+b+c |  |  |  | 14490.83
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 38.41 |  | 3840.83
|  | (f) Total = d+e+f |  |  |  | 14529.24
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 14529.24
|  | Rate per joint = h/10 |  |  |  | 1452.92
| xx | 800 mm dia pipe
Foreman (work inspector) Non technical
|  | Plumber 1st class | day | 2.35 | 515 | 1210.25
|  | Plumber 2nd class | day | 4.7 | 400 | 1880
|  | Foreman (work inspector) Non technical | day | 0.65 | 460 | 299
b) Material
|  | Rubber gasket | each | 10 | 1277 | 12770
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 51.0044 | 2550.22
|  | (d) Total = a+b+c |  |  |  | 18709.47
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 59.39 |  | 5939.47
|  | (f) Total = d+e |  |  |  | 18768.86
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 18768.86
|  | Rate per joint = h/10 |  |  |  | 1876.89
| xxi | 900 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 2.75 | 515 | 1416.25
|  | Plumber 2nd class | day | 5.5 | 400 | 2200
|  | Foreman (work inspector) Non technical | day | 0.7 | 460 | 322
b) Material
|  | Rubber gasket | each | 10 | 1541 | 15410
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 57.38 | 2869
|  | (d) Total = a+b+c |  |  |  | 22217.25
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 68.07 |  | 6807.25
|  | (f) Total = d+e+f |  |  |  | 22285.32
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 22285.32
|  | Rate per joint = h/10 |  |  |  | 2228.53
| xxii | 1000 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 3 | 515 | 1545
|  | Plumber 2nd class | day | 6 | 400 | 2400
|  | Foreman (work inspector) Non technical | day | 0.75 | 460 | 345
b) Material
|  | Rubber gasket | each | 10 | 1696 | 16960
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 50 | 63.7556 | 3187.77
|  | (d) Total = a+b+c |  |  |  | 24437.77
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 74.78 |  | 7477.77
|  | (f) Total = d+e+f |  |  |  | 24512.55
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 24512.55
|  | Rate per joint = h/10 |  |  |  | 2451.26
PHE-JCIF-5 | 5 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials such as bolts, rubber insertion, white lead including filling with water, with lead up to 500 meters and testing to required pressure complete. (Reference to specifications. BIS No.3114/1994.) | [7 empty] | CI FLANGED JOINTING
Details of cost for 10 joints
| i | 80 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.09 | 540 | 48.6
|  | Plumber 2nd class | day | 0.21 | 425 | 89.25
|  | Man mazdoor | day | 0.8 | 400 | 320
b) Material
|  | Bolts and nuts 16mm dia 60mm long | kg | 6.8 | 84 | 571.2
|  | Rubber insertion 5mm thick | kg | 2.125 | 57 | 121.12
|  | White lead | kg | 0.1 | 103 | 10.3
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 5.1004 | 140.26
|  | (d) Total = a+b+c |  |  |  | 1300.73
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 5.98 |  | 598.11
|  | (f) Total = d+e+f |  |  |  | 1306.71
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 1306.71
|  | Rate per joint = h/10 |  |  |  | 130.67
| ii | 100 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.15 | 540 | 81
|  | Plumber 2nd class | day | 0.35 | 425 | 148.75
|  | Man mazdoor | day | 1 | 400 | 400
b) Material
|  | Bolts and nuts 16mm dia 60mm long | kg | 13.6 | 84 | 1142.4
|  | Rubber insertion 5mm thick | kg | 2.54 | 57 | 144.78
|  | White lead | kg | 0.15 | 103 | 15.45
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 6.3756 | 175.32
|  | (d) Total = a+b+c |  |  |  | 2107.7
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 8.05 |  | 805.07
|  | (f) Total = d+e+f |  |  |  | 2115.75
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 2115.75
|  | Rate per joint = h/10 |  |  |  | 211.58
| iii | 125 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.15 | 540 | 81
|  | Plumber 2nd class | day | 0.35 | 425 | 148.75
|  | Man mazdoor | day | 1 | 400 | 400
b) Material
|  | Bolts and nuts 16mm dia 60mm long | kg | 13.6 | 84 | 1142.4
|  | Rubber insertion 5mm thick | kg | 3.14 | 57 | 178.98
|  | White lead |  | 0.18 | 103 | 18.54
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 7.9694 | 219.15
|  | (d) Total = a+b+c |  |  |  | 2188.82
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 8.49 |  | 848.9
|  | (f) Total = d+e+f |  |  |  | 2197.31
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 2197.31
|  | Rate per joint = h/10 |  |  |  | 219.73
| iv | 150 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.18 | 540 | 97.2
|  | Plumber 2nd class | day | 0.42 | 425 | 178.5
|  | Man mazdoor | day | 1.1 | 400 | 440
b) Material
|  | Bolts and nuts 20mm dia 65mm long | kg | 24 | 84 | 2016
|  | Rubber insertion 5mm thick | kg | 4.3 | 57 | 245.1
|  | White lead |  | 0.2 | 103 | 20.6
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 9.5633 | 262.99
|  | (d) Total = a+b+c |  |  |  | 3260.39
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 9.79 |  | 978.69
|  | (f) Total = d+e+f |  |  |  | 3270.18
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 3270.18
|  | Rate per joint = h/10 |  |  |  | 327.02
| v | 200 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.18 | 540 | 97.2
|  | Plumber 2nd class | day | 0.42 | 425 | 178.5
|  | Man mazdoor | day | 1.1 | 400 | 440
b) Material
|  | Bolts and nuts 20mm dia 70mm long | kg | 25.2 | 84 | 2116.8
|  | Rubber insertion 5mm thick | kg | 6.16 | 57 | 351.12
|  | White lead |  | 0.25 | 103 | 25.75
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 12.7511 | 350.65
|  | (d) Total = a+b+c |  |  |  | 3560.02
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 10.66 |  | 1066.35
|  | (f) Total = d+e+f |  |  |  | 3570.68
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 3570.68
|  | Rate per joint = h/10 |  |  |  | 357.07
| vi | 250 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.2 | 540 | 108
|  | Plumber 2nd class | day | 0.42 | 425 | 178.5
|  | Man mazdoor | day | 1.2 | 400 | 480
b) Material
|  | Bolts and nuts 20mm dia 75mm long | kg | 39.6 | 84 | 3326.4
|  | Rubber insertion 5mm thick | kg | 8.5 | 57 | 484.5
|  | White lead |  | 0.3 | 103 | 30.9
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 15.9389 | 438.31
|  | (d) Total = a+b+c |  |  |  | 5046.61
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 12.05 |  | 1204.81
|  | (f) Total = d+e+f |  |  |  | 5058.66
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 5058.66
|  | Rate per joint = h/10 |  |  |  | 505.87
| vii | 300 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.24 | 540 | 129.6
|  | Plumber 2nd class | day | 0.56 | 425 | 238
|  | Man mazdoor | day | 1.2 | 400 | 480
b) Material
|  | Bolts and nuts 20mm dia 75mm long | kg | 39.6 | 84 | 3326.4
|  | Rubber insertion 5mm thick | kg | 10.28 | 57 | 585.96
|  | White lead |  | 0.35 | 103 | 36.05
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 19.1267 | 525.98
|  | (d) Total = a+b+c |  |  |  | 5321.99
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 13.74 |  | 1373.58
|  | (f) Total = d+e+f |  |  |  | 5335.73
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 5335.73
|  | Rate per joint = h/10 |  |  |  | 533.57
| viii | 350 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.3 | 540 | 162
|  | Plumber 2nd class | day | 0.6 | 425 | 255
|  | Man mazdoor | day | 1.5 | 400 | 600
b) Material
|  | Bolts and nuts 20mm dia 80mm long | kg | 54.4 | 84 | 4569.6
|  | Rubber insertion 8mm thick | kg | 21.26 | 57 | 1211.82
|  | White lead |  | 0.4 | 103 | 41.2
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 22.3144 | 613.64
|  | (d) Total = a+b+c |  |  |  | 7453.26
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 16.31 |  | 1630.64
|  | (f) Total = d+e+f |  |  |  | 7469.57
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 7469.57
|  | Rate per joint = h/10 |  |  |  | 746.96
| ix | 400 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.3 | 540 | 162
|  | Plumber 2nd class | day | 0.7 | 425 | 297.5
|  | Man mazdoor | day | 1.5 | 400 | 600
b) Material
|  | Bolts and nuts 24mm dia 85mm long | kg | 98.4 | 84 | 8265.6
|  | Rubber insertion 8mm thick | kg | 27.64 | 57 | 1575.48
|  | White lead |  | 0.45 | 103 | 46.35
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 25.5022 | 701.31
|  | (d) Total = a+b+c |  |  |  | 11648.24
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 17.61 |  | 1760.81
|  | (f) Total = d+e+f |  |  |  | 11665.85
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 11665.85
|  | Rate per joint = h/10 |  |  |  | 1166.59
| x | 450 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.36 | 540 | 194.4
|  | Plumber 2nd class | day | 0.84 | 425 | 357
|  | Man mazdoor | day | 1.7 | 400 | 680
b) Material
|  | Bolts and nuts 24mm dia 85mm long | kg | 123 | 84 | 10332
|  | Rubber insertion 8mm thick | kg | 22.66 | 57 | 1291.62
|  | White lead |  | 0.5 | 103 | 51.5
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 28.69 | 788.97
|  | (d) Total = a+b+c |  |  |  | 13695.49
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 20.2 |  | 2020.37
|  | (f) Total = d+e+f |  |  |  | 13715.69
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 13715.69
|  | Rate per joint = h/10 |  |  |  | 1371.57
| xi | 500 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.39 | 540 | 210.6
|  | Plumber 2nd class | day | 0.91 | 425 | 386.75
|  | Man mazdoor | day | 1.8 | 400 | 720
b) Material
|  | Bolts and nuts 24mm dia 90mm long | kg | 134 | 84 | 11256
|  | Rubber insertion 8mm thick | kg | 38.19 | 57 | 2176.83
|  | White lead |  | 0.55 | 103 | 56.65
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 31.8778 | 876.63
|  | (d) Total = a+b+c |  |  |  | 15683.46
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 21.94 |  | 2193.98
|  | (f) Total = d+e+f |  |  |  | 15705.4
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 15705.4
|  | Rate per joint = h/10 |  |  |  | 1570.54
| xii | 600 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.45 | 540 | 243
|  | Plumber 2nd class | day | 1.05 | 425 | 446.25
|  | Man mazdoor | day | 2 | 400 | 800
b) Material
|  | Bolts and nuts 24mm dia 90mm long | kg | 192 | 84 | 16128
|  | Rubber insertion 8mm thick | kg | 51.71 | 57 | 2947.47
|  | White lead |  | 0.6 | 103 | 61.8
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 38.2533 | 1051.96
|  | (d) Total = a+b+c |  |  |  | 21678.48
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 25.41 |  | 2541.21
|  | (f) Total = d+e+f |  |  |  | 21703.89
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 21703.89
|  | Rate per joint = h/10 |  |  |  | 2170.39
| xiii | 700 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.51 | 540 | 275.4
|  | Plumber 2nd class | day | 1.19 | 425 | 505.75
|  | Man mazdoor | day | 2.2 | 400 | 880
b) Material
|  | Bolts and nuts 24mm dia 90mm long | kg | 244.8 | 84 | 20563.2
|  | Rubber insertion 8mm thick | kg | 68.91 | 57 | 3927.87
|  | White lead |  | 0.7 | 103 | 72.1
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 44.6289 | 1227.29
|  | (d) Total = a+b+c |  |  |  | 27451.61
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 28.88 |  | 2888.44
|  | (f) Total = d+e+f |  |  |  | 27480.49
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 27480.49
|  | Rate per joint = h/10 |  |  |  | 2748.05
| xiv | 750 mm dia pipe
a) Labour
|  | Plumber 1st class | day | 0.51 | 515 | 262.65
|  | Plumber 2nd class | day | 1.19 | 400 | 476
|  | Man mazdoor | day | 2.2 | 350 | 770
b) Material
|  | Bolts and nuts 24mm dia 90mm long | kg | 260.4 | 129 | 33591.6
|  | Rubber insertion 8mm thick | kg | 78.43 | 108 | 8470.44
|  | White lead |  | 0.75 | 113 | 84.75
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 27.5 | 47.8167 | 1314.95
|  | (d) Total = a+b+c |  |  |  | 44970.39
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 28.24 |  | 2823.6
|  | (f) Total = d+e+f |  |  |  | 44998.63
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 10 joints (f+g) |  |  |  | 44998.63
|  | Rate per joint = h/10 |  |  |  | 4499.86
PHE-LRCS-6 | 6 | Lowering the RCC S/S pipes carefully into the trenches laying them true to alignment and gradient, jointing with rubber rings and testing including filling with water with a water lead upto 500 meters including cost of rubber rings as per BIS No. 783/1985 | [7 empty] | RCC S/S
Unit= 1 rmt
Taking out put 100 rmt
| i | 80 mm dia |  | NP2 PIPES
a) Labour
|  | Mason 1st class | day | 0.78 | 445 | 347.1
|  | Mason 2nd class | day | 1.8 | 405 | 729
|  | Man mazdoor | day | 5 | 350 | 1750
|  | Woman mazdoor(water carrier) | day | 1.3 | 350 | 455
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 26 | 1300
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 5.1004 | 510.04
|  | (d) Total = a+b+c |  |  |  | 5091.14
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 37.91 |  | 3791.14
|  | (f) Total = d+e |  |  |  | 5129.05
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 5129.05
|  | Rate per rmt = h/100 |  |  |  | 51.29
| ii | 100 mm dia
a) Labour
|  | Mason 1st class | day | 0.96 | 445 | 427.2
|  | Mason 2nd class | day | 2.24 | 405 | 907.2
|  | Man mazdoor | day | 6.3 | 350 | 2205
|  | Woman mazdoor(water carrier) | day | 1.6 | 350 | 560
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 32 | 1600
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 6.3756 | 637.55
|  | (d) Total = a+b+c |  |  |  | 6336.95
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 47.37 |  | 4736.95
|  | (f) Total = d+e |  |  |  | 6384.32
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 6384.32
|  | Rate per rmt = h/100 |  |  |  | 63.84
| iii | 150 mm dia
a) Labour
|  | Mason 1st class | day | 1.17 | 445 | 520.65
|  | Mason 2nd class | day | 2.73 | 405 | 1105.65
|  | Man mazdoor | day | 7.8 | 350 | 2730
|  | Woman mazdoor(water carrier) | day | 1.6 | 350 | 560
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 57 | 2850
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 9.5633 | 0
|  | (d) Total = a+b+c |  |  |  | 7766.3
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 49.16 |  | 4916.3
|  | (f) Total = d+e |  |  |  | 7815.46
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 7815.46
|  | Rate per rmt = h/100 |  |  |  | 78.15
| iv | 200 mm dia
a) Labour
|  | Mason 1st class | day | 1.17 | 445 | 520.65
|  | Mason 2nd class | day | 2.73 | 405 | 1105.65
|  | Man mazdoor | day | 7.8 | 350 | 2730
|  | Woman mazdoor(water carrier) | day | 1.6 | 350 | 560
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 67 | 3350
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 12.7511 | 1275.11
|  | (d) Total = a+b+c |  |  |  | 9541.41
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 61.91 |  | 6191.41
|  | (f) Total = d+e |  |  |  | 9603.32
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 9603.32
|  | Rate per rmt = h/100 |  |  |  | 96.03
| v | 225 mm dia
a) Labour
|  | Mason 1st class | day | 1.62 | 445 | 720.9
|  | Mason 2nd class | day | 3.78 | 405 | 1530.9
|  | Man mazdoor | day | 10.5 | 350 | 3675
|  | Woman mazdoor(water carrier) | day | 2.3 | 350 | 805
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 74 | 3700
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 14.345 | 1434.5
|  | (d) Total = a+b+c |  |  |  | 11866.3
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 81.66 |  | 8166.3
|  | (f) Total = d+e |  |  |  | 11947.96
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 11947.96
|  | Rate per rmt = h/100 |  |  |  | 119.48
| vi | 250 mm dia
a) Labour
|  | Mason 1st class | day | 1.62 | 445 | 720.9
|  | Mason 2nd class | day | 3.78 | 405 | 1530.9
|  | Man mazdoor | day | 10.5 | 350 | 3675
|  | Woman mazdoor(water carrier) | day | 2.3 | 350 | 805
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 50 | 83 | 4150
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 15.9389 | 1593.88
|  | (d) Total = a+b+c |  |  |  | 12475.68
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 83.26 |  | 8325.68
|  | (f) Total = d+e |  |  |  | 12558.94
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 12558.94
|  | Rate per rmt = h/100 |  |  |  | 125.59
| vii | 300 mm dia
a) Labour
|  | Mason 1st class | day | 1.75 | 445 | 778.75
|  | Mason 2nd class | day | 4.14 | 405 | 1676.7
|  | Man mazdoor | day | 11.6 | 350 | 4060
|  | Woman mazdoor(water carrier) | day | 2.3 | 350 | 805
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 101 | 4040
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 19.1267 | 1912.66
|  | (d) Total = a+b+c |  |  |  | 13273.11
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 92.33 |  | 9233.11
|  | (f) Total = d+e |  |  |  | 13365.44
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 13365.44
|  | Rate per rmt = h/100 |  |  |  | 133.65
| viii | 350 mm dia
a) Labour
|  | Mason 1st class | day | 1.9 | 445 | 845.5
|  | Mason 2nd class | day | 4.5 | 405 | 1822.5
|  | Man mazdoor | day | 12.7 | 350 | 4445
|  | Woman mazdoor(water carrier) | day | 2.4 | 350 | 840
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 117 | 4680
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 22.3144 | 2231.44
|  | (d) Total = a+b+c |  |  |  | 14864.44
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 101.84 |  | 10184.44
|  | (f) Total = d+e |  |  |  | 14966.28
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 14966.28
|  | Rate per rmt = h/100 |  |  |  | 149.66
| ix | 400 mm dia
a) Labour
|  | Mason 1st class | day | 2.1 | 445 | 934.5
|  | Mason 2nd class | day | 4.9 | 405 | 1984.5
|  | Man mazdoor | day | 13.9 | 350 | 4865
|  | Woman mazdoor(water carrier) | day | 2.9 | 350 | 1015
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 129 | 5160
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 25.5022 | 2550.22
|  | (d) Total = a+b+c |  |  |  | 16509.22
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 113.49 |  | 11349.22
|  | (f) Total = d+e |  |  |  | 16622.71
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 16622.71
|  | Rate per rmt = h/100 |  |  |  | 166.23
| x | 450 mm dia
a) Labour
|  | Mason 1st class | day | 2.25 | 445 | 1001.25
|  | Mason 2nd class | day | 5.25 | 405 | 2126.25
|  | Man mazdoor | day | 15 | 350 | 5250
|  | Woman mazdoor(water carrier) | day | 3.3 | 350 | 1155
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 146 | 5840
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 28.69 | 2869
|  | (d) Total = a+b+c |  |  |  | 18241.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 124.02 |  | 12401.5
|  | (f) Total = d+e |  |  |  | 18365.52
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 18365.52
|  | Rate per rmt = h/100 |  |  |  | 183.66
| xi | 500 mm dia
a) Labour
|  | Mason 1st class | day | 2.43 | 445 | 1081.35
|  | Mason 2nd class | day | 5.67 | 405 | 2296.35
|  | Man mazdoor | day | 16.2 | 350 | 5670
|  | Woman mazdoor(water carrier) | day | 3.3 | 350 | 1155
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 191 | 7640
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 31.8778 | 3187.77
|  | (d) Total = a+b+c |  |  |  | 21030.47
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 133.9 |  | 13390.47
|  | (f) Total = d+e |  |  |  | 21164.37
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 21164.37
|  | Rate per rmt = h/100 |  |  |  | 211.64
| xii | 600 mm dia
a) Labour
|  | Mason 1st class | day | 2.75 | 445 | 1223.75
|  | Mason 2nd class | day | 6.45 | 405 | 2612.25
|  | Man mazdoor | day | 16.3 | 350 | 5705
|  | Woman mazdoor(water carrier) | day | 3.3 | 350 | 1155
b) Material
|  | Rubber rings conforming BIS 5382/1985 | each | 40 | 251 | 10040
c) Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment, labour and Materials needed for testing (as per Sub Analysis 2 A) | rm | 100 | 38.2533 | 3825.33
|  | (d) Total = a+b+c |  |  |  | 24561.33
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 145.21 |  | 14521.33
|  | (f) Total = d+e |  |  |  | 24706.54
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 24706.54
|  | Rate per rmt = h/100 |  |  |  | 247.07
|  | 700 mm dia |  |  |  | 292 |  | AS PER SSR pg.297 item 11(b)
|  | 800 mm dia |  |  |  | 350 |  | AS PER SSR pg.297 item 11(b)
|  | 900 mm dia |  |  |  | 420 |  | AS PER SSR pg.297 item 11(b)
|  | 1000 mm dia |  |  |  | 503 |  | AS PER SSR pg.297 item 11(b)
PHE-LJGI-7 | 7 | Lowering and Jointing G.I. pipes and specials / fittings including excavation of trench of 0.5m width and 0.50 m depth in all soils except rock requiring blasting and refilling trenches after laying and jointing pipes and also including cost of jointing materials but excluding the cost of pipes. Reference to specifications. BIS No.783/85 |  |  |  |  | NOT UPDATED |  |  | GI PIPES
Details of cost for 10m
| i | 15mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.06 | 400 | 24
|  | Man mazdoor | day | 0.16 | 350 | 56
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10 | 167 | 1670
|  | white lead, hemp yarn, oil etc. | L.S. |  | 72
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 2068.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 20.69
|  | (f) Total = d+e |  |  |  | 2089.19
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 2089.19
|  | Rate per rmt = h/100 |  |  |  | 20.89
| ii | 20mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.06 | 400 | 24
|  | Man mazdoor | day | 0.16 | 350 | 56
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 398.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 3.99
|  | (f) Total = d+e |  |  |  | 402.49
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 402.49
|  | Rate per rmt = h/100 |  |  |  | 4.02
| iii | 25mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.12 | 400 | 48
|  | Man mazdoor | day | 0.25 | 350 | 87.5
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10 | 252
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 454
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 4.54
|  | (f) Total = d+e |  |  |  | 458.54
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 458.54
|  | Rate per rmt = h/100 |  |  |  | 4.59
| iv | 32mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.12 | 400 | 48
|  | Man mazdoor | day | 0.25 | 350 | 87.5
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 454
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 4.54
|  | (f) Total = d+e |  |  |  | 458.54
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 458.54
|  | Rate per rmt = h/100 |  |  |  | 4.59
| v | 40mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.16 | 400 | 64
|  | Man mazdoor | day | 0.33 | 350 | 115.5
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10 | 381 | 3810
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 4308
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 43.08
|  | (f) Total = d+e |  |  |  | 4351.08
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 4351.08
|  | Rate per rmt = h/100 |  |  |  | 43.51
| vi | 50mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.16 | 400 | 64
|  | Man mazdoor | day | 0.33 | 350 | 115.5
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 498
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 4.98
|  | (f) Total = d+e |  |  |  | 502.98
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 502.98
|  | Rate per rmt = h/100 |  |  |  | 5.03
| vii | 65mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.25 | 400 | 100
|  | Man mazdoor | day | 0.66 | 350 | 231
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 649.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 6.5
|  | (f) Total = d+e |  |  |  | 656
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 656
|  | Rate per rmt = h/100 |  |  |  | 6.56
| viii | 80mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.25 | 400 | 100
|  | Man mazdoor | day | 0.66 | 350 | 231
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 649.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 6.5
|  | (f) Total = d+e |  |  |  | 656
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 656
|  | Rate per rmt = h/100 |  |  |  | 6.56
| ix | 100mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.37 | 400 | 148
|  | Man mazdoor | day | 0.97 | 350 | 339.5
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10 | 650 | 6500
|  | white lead, hemp yarn, oil etc. | L.S. |  | 100 | 100
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 7406
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 74.06
|  | (f) Total = d+e |  |  |  | 7480.06
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 7480.06
|  | Rate per rmt = h/100 |  |  |  | 74.8
| x | 150mm dia nominal bore
a) Labour
|  | Plumber 2nd class | day | 0.58 | 400 | 232
|  | Man mazdoor | day | 1.54 | 350 | 539
|  | E.W.Excavation & refilling 10x0.50x0.50=2.50cum | cum | 2.5 | 127.4 | 318.5
b) Material
|  | G.I. pipes | m | 10
|  | white lead, hemp yarn, oil etc. | L.S.
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 1089.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 10.9
|  | (f) Total = d+e |  |  |  | 1100.4
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | (h) Cost for 100 rmt (f+g) |  |  |  | 1100.4
|  | Rate per rmt = h/100 |  |  |  | 11
PHE-GIDM-8 | 8 | Making connection of G.I. distribution branch with G.I. main by providing and fixing tee, including cutting and threading the pipes and fixing tee etc., complete. Reference to specifications. BIS No.783/85 |  |  |  |  | NOT UPDATED
Details of cost for 1 No
| i | 25mm branch from 40mm nominal dia main
a) Labour
|  | Plumber 2nd class | day | 0.33 | 400 | 132
|  | Man mazdoor | day | 0.33 | 350 | 115.5
|  | b) Material |  |  |  | 0
|  | G.I. tee 25mm dia. | Each | 1
|  | G.I. Jam nut 25mm | Each | 1
Sundries
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 247.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 2.48
|  | (f) Total = d+e |  |  |  | 249.98
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1No (f+g) |  |  |  | 249.98
| ii | 50 mm branch from 80 mm nominal dia main |  |  |  | 2.5
a) Labour
|  | Plumber 2nd class | day | 0.45 | 400 | 180
|  | Man mazdoor | day | 0.45 | 350 | 157.5
|  | b) Material |  |  |  | 0
|  | G.I. tee 50mm dia. | Each | 1
|  | G.I. Jam nut 50mm | Each | 1
Sundries
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 337.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 3.38
|  | (f) Total = d+e |  |  |  | 340.88
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1No (f+g) |  |  |  | 340.88
| iii | 100mm branch from 150mm nominal dia main |  |  |  | 3.41
a) Labour
|  | Plumber 2nd class | day | 0.45 | 400 | 180
|  | Man mazdoor | day | 0.45 | 350 | 157.5
b) Material
|  | G.I. tee 150mm dia. | Each | 1
|  | G.I. Jam nut 150mm | Each | 1
Sundries
c) Machinery
Nil
|  | (d) Total = a+b+c |  |  |  | 337.5
|  | (e) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 3.38
|  | (f) Total = d+e |  |  |  | 340.88
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1No (f+g) |  |  |  | 340.88
PHE-LACP-9 | 9 | Lowering and laying AC pressure pipes (class 5 & 10) in ready made trenches true to alignment and gradient including all sundries but excluding conveyance from source of supply. Reference to specifications BIS 6530/72 | [7 empty] | AC PIPES LOWERING
Details of cost for 1rmt
Note : The Coat of lowring, laying is taken for 1 kg weight as per sub-analysis made for CI SS ends.
| A | Class 10 & 15 pipes :
| i | 80 mm dia pipe
Weight of 1m length = (6.225+6.225)/2 = 6.225 kgs
|  | (a) Labour charges for laying | kgs | 6.225 | 1.34 | 8.34
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 8.34
| ii | 100 mm dia pipe
Weight of 1m length = (7.8+8.18)/2 = 7.99 kgs
|  | (a) Labour charges for laying | kgs | 7.99 | 1.34 | 10.7
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 10.7
| iii | 125 mm dia pipe
Weight of 1m length = (9.8+10.725)/2 = 10.262 kgs
|  | (a) Labour charges for laying | kgs | 10.262 | 1.34 | 13.75
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 13.75
| iv | 150 mm dia pipe
Weight of 1m length = (12.15+15.18)/2 = 13.665 kgs
|  | (a) Labour charges for laying | kgs | 13.665 | 1.34 | 18.31
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 18.31
| v | 200 mm dia pipe
Weight of 1m length = (19.1+25.3)/2 = 22.2 kgs
|  | (a) Labour charges for laying | kgs | 22.2 | 1.34 | 29.74
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 29.74
| vi | 250 mm dia pipe
Weight of 1m length = (24.9+32)/2 = 28.450 kgs
|  | (a) Labour charges for laying | kgs | 28.45 | 1.34 | 38.12
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 38.12
| vii | 300 mm dia pipe
Weight of 1m length = (32.2+44.925)/2 =38.562 kgs
|  | (a) Labour charges for laying | kgs | 38.562 | 1.34 | 51.67
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 51.67
| viii | 350 mm dia pipe
Weight of 1m length = (13.6+54.875)/2 = 47.237 kgs
|  | (a) Labour charges for laying | kgs | 47.237 | 1.34 | 63.29
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 63.29
| ix | 400 mm dia pipe
Weight of 1m length = (49.125+71.425)/2 =60.275 kgs
|  | (a) Labour charges for laying | kgs | 60.275 | 1.34 | 80.76
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 80.76
| x | 450 mm dia pipe
Weight of 1m length = (59.225+84.025)/2 = 71.625 kgs
|  | (a) Labour charges for laying | kgs | 71.625 | 1.34 | 95.97
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 95.97
| xi | 500 mm dia pipe
Weight of 1m length = (73.2+104.25)/2 = 88.725 kgs
|  | (a) Labour charges for laying | kgs | 88.725 | 1.34 | 118.89
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 118.89
| xii | 600 mm dia pipe
Weight of 1m length = (102.5+148.025)/2 = 125.262 kgs
|  | (a) Labour charges for laying | kgs | 125.262 | 1.34 | 167.85
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 167.85
| B | Class 20 & 25 pipes :
| i | 80 mm dia pipe
Weight of 1m length = (6.23+8.525)/2 = 7.378 kgs
|  | (a) Labour charges for laying | kgs | 7.378 | 1.34 | 9.88
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 9.88
| ii | 100 mm dia pipe
Weight of 1m length = (10.35+12.825)/2 =11.587 kgs
|  | (a) Labour charges for laying | kgs | 11.587 | 1.34 | 15.52
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 15.52
| iii | 125 mm dia pipe
Weight of 1m length = (13.35+16.825)/2 = 15.087 kgs
|  | (a) Labour charges for laying | kgs | 15.087 | 1.34 | 20.21
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 20.21
| iv | 150 mm dia pipe
Weight of 1m length = (18.9+23.65)/2 = 21.275 kgs
|  | (a) Labour charges for laying | kgs | 21.275 | 1.34 | 28.5
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 28.5
| v | 200 mm dia pipe
Weight of 1m length = (32.1+40.75)/2 = 36.425 kgs
|  | (a) Labour charges for laying | kgs | 36.425 | 1.34 | 48.8
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 48.8
| vi | 250 mm dia pipe
Weight of 1m length = (41.175+51.65)/2 = 46.412 kgs
|  | (a) Labour charges for laying | kgs | 46.412 | 1.34 | 62.19
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 62.19
| vii | 300 mm dia pipe
Weight of 1m length = (58.1+74.05)/2 = 66.075 kgs
|  | (a) Labour charges for laying | kgs | 66.075 | 1.34 | 88.54
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 88.54
| viii | 350 mm dia pipe
Weight of 1m length = (71.275+81.55)/2 = 76.412 kgs
|  | (a) Labour charges for laying | kgs | 76.412 | 1.34 | 102.39
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 102.39
| ix | 400 mm dia pipe
Weight of 1m length = (93.05+115.4)/2 = 104.225 kgs
|  | (a) Labour charges for laying | kgs | 104.225 | 1.34 | 139.66
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 139.66
| x | 450 mm dia pipe
Weight of 1m length = (111.275+139.45)/2 = 125.36 kgs
|  | (a) Labour charges for laying | kgs | 125.36 | 1.34 | 167.98
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 167.98
| xi | 500 mm dia pipe
Weight of 1m length = (136.325+171.275)/2 = 153.8 kgs
|  | (a) Labour charges for laying | kgs | 153.8 | 1.34 | 206.09
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 206.09
| xii | 600 mm dia pipe
Weight of 1m length = (192.925+245.9)/2 = 219.412 kgs
|  | (a) Labour charges for laying | kgs | 219.412 | 1.34 | 294.01
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre |  |  |  | 294.01
PHE-JACP-10 | 10 | Jointing A.C. pressure pipes with A.C. coupling or C.I. detachable joints complete with rubber rings including filling with water, with a water lead up to 500m and testing to required pressure etc., complete but excluding cost of jointing materials and conveyance of pipe from source of supply. Reference to specifications BIS No.6530/72 (Labour Charges Only) | [7 empty] | AC JOINTING
Detail of cost for 10 joints
Sub Analysis : For Machinery used for testing
OBSERVED DATA FOR TESTING OF 450 MM DIA PSC MAIN : Pumping main to Hydralic field test pressure including transportation of Water with minimum lead of 500 M
(Length = 500 Mts) taking out put / 500 Mts. Unit = 1 Rmt.
Machinery
|  | Hire chargers for Hydralic field test pressure testing including transportation of water @ Rs. 1200/- (1000+200) / day | days | 3 | 1200 | 3600
Materials
|  | Pressure guage | Nos | 0.05 | 400 | 20
|  | 3/4" G.I. Pipe | Mts | 3 | 172.5 | 517.5
|  | Specials | Ls |  |  | 5.375
|  | Dummies | No. | 0.1 | 40 | 4
|  | Diesel (2 Lts. / Hr) 30 Hrs. | Lts. | 60 | 61.04 | 3662.4
|  | (T) Total Rate per 500 Mts. |  |  |  | 7809.275
|  | (r) Rate per 1 Rmt for 450 mm dia |  |  |  | 15.62
|  | (R) Rate per 1 Rmt for 10 mm dia = (10/450) x r |  |  |  | 0.35
| i | 80 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.18 | 515 | 92.7
|  | Plumber 2nd class | day | 0.42 | 400 | 168
|  | Man mazdoor | day | 1.6 | 350 | 560
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 5.1004 | 204.01
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 10.2471
|  | (d) Total = a+b+c |  |  |  | 1034.9571
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 1034.9571
|  | Rate per each joint = f/10 |  |  |  | 103.4957
| ii | 100 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.3 | 515 | 154.5
|  | Plumber 2nd class | day | 0.7 | 400 | 280
|  | Man mazdoor | day | 2 | 350 | 700
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 6.3756 | 255.02
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 13.8952
|  | (d) Total = a+b+c |  |  |  | 1403.4152
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 1403.4152
|  | Rate per each joint = f/10 |  |  |  | 140.3415
| iii | 125 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.3 | 515 | 154.5
|  | Plumber 2nd class | day | 0.7 | 400 | 280
|  | Man mazdoor | day | 2 | 350 | 700
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 7.9694 | 318.77
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 14.5327
|  | (d) Total = a+b+c |  |  |  | 1467.8027
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 1467.8027
|  | Rate per each joint = f/10 |  |  |  | 146.7803
| iv | 150 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.36 | 515 | 185.4
|  | Plumber 2nd class | day | 0.84 | 400 | 336
|  | Man mazdoor | day | 2.2 | 350 | 770
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 9.5633 | 382.53
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 16.7393
|  | (d) Total = a+b+c |  |  |  | 1690.6693
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 1690.6693
|  | Rate per each joint = f/10 |  |  |  | 169.0669
| v | 200 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.36 | 515 | 185.4
|  | Plumber 2nd class | day | 0.84 | 400 | 336
|  | Man mazdoor | day | 2.2 | 350 | 770
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 12.7511 | 510.04
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 18.0144
|  | (d) Total = a+b+c |  |  |  | 1819.4544
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 1819.4544
|  | Rate per each joint = f/10 |  |  |  | 181.9454
| vi | 250 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.48 | 515 | 247.2
|  | Plumber 2nd class | day | 1.12 | 400 | 448
|  | Man mazdoor | day | 2.6 | 350 | 910
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 15.9389 | 637.55
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 22.4275
|  | (d) Total = a+b+c |  |  |  | 2265.1775
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 2265.1775
|  | Rate per each joint = f/10 |  |  |  | 226.5177
| vii | 300 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.48 | 515 | 247.2
|  | Plumber 2nd class | day | 1.12 | 400 | 448
|  | Man mazdoor | day | 2.6 | 350 | 910
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 19.1267 | 765.06
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 23.7026
|  | (d) Total = a+b+c |  |  |  | 2393.9626
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 2393.9626
|  | Rate per each joint = f/10 |  |  |  | 239.3963
| viii | 350 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.6 | 515 | 309
|  | Plumber 2nd class | day | 1.4 | 400 | 560
|  | Man mazdoor | day | 3 | 350 | 1050
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment, labour and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 22.3144 | 892.57
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 28.1157
|  | (d) Total = a+b+c |  |  |  | 2839.6857
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 2839.6857
|  | Rate per each joint = f/10 |  |  |  | 283.9686
| ix | 400 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.6 | 515 | 309
|  | Plumber 2nd class | day | 1.4 | 400 | 560
|  | Man mazdoor | day | 3 | 350 | 1050
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 25.5022 | 1020.08
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 29.3908
|  | (d) Total = a+b+c |  |  |  | 2968.4708
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 2968.4708
|  | Rate per each joint = f/10 |  |  |  | 296.8471
| x | 450 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.72 | 515 | 370.8
|  | Plumber 2nd class | day | 1.68 | 400 | 672
|  | Man mazdoor | day | 3.4 | 350 | 1190
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 28.69 | 1147.6
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 33.804
|  | (d) Total = a+b+c |  |  |  | 3414.204
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 3414.204
|  | Rate per each joint = f/10 |  |  |  | 341.4204
| xi | 500 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.72 | 515 | 370.8
|  | Plumber 2nd class | day | 1.68 | 400 | 672
|  | Man mazdoor | day | 3.4 | 350 | 1190
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 31.8778 | 1275.11
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 35.0791
|  | (d) Total = a+b+c |  |  |  | 3542.9891
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 3542.9891
|  | Rate per each joint = f/10 |  |  |  | 354.2989
| xii | 600 mm dia meter pipe
(a) Labour
|  | Plumber 1st class | day | 0.84 | 515 | 432.6
|  | Plumber 2nd class | day | 1.96 | 400 | 784
|  | Man mazdoor | day | 3.8 | 350 | 1330
Total
|  | (b) Machinery for Testing of Pipelines with required pressure as per relevant IS Specification including hire charges of testing equipment and transportation of water upto 500 M lead Materials needed for testing (as per Sub Analysis 11 A) | rm | 40 | 38.2533 | 1530.13
|  | (c) Add for water charges @ 1% on Labour & Testing Charges |  |  |  | 40.7673
|  | (d) Total = a+b+c |  |  |  | 4117.4973
|  | (e) Overheads & Contractors Profit |  |  |  | 0
|  | (f) Cost for 10 joints = d+e |  |  |  | 4117.4973
|  | Rate per each joint = f/10 |  |  |  | 411.7497
PHE-LJUP-11 | 11 | Lowering, laying, jointing and testing to hydralic test pressure including cost of water with minimum water lead of 500m for UPVC pressure pipes in ready made trenches true to alignment and gradient including all sundries but excluding cost & conveyance of pipes from source of supply and jointing materials as per BIS No. 7634 - Part III - 1975 | [7 empty] | PVC PIPES
Sub Analysis for 160 mm Dia :
Taking output : Length - 500 m ; Joints - 83 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 7 | 605 | 4235
Jointing
|  | Fitter | day | 2 | 775 | 1550 | P -39
|  | Mazdoor | day | 4 | 605 | 2420
Testing
|  | Testing of Pipelines with required pressure as per relevant IS Specification including filling with water with a water lead upto 500 M, including hire charges of testing equipment and labour, Materials needed for testing (as per Sub Analysis 2 A) | rm | 500 | 10.2009 | 5100.44
|  | Total |  |  |  | 13305.44
(b) Material
|  | Add for Water charges at 1% on Labour & Testing | Lt |  |  | 133.05
|  | (c) Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 13438.49
|  | Rate per RM =d/500 |  |  |  | 26.88
|  | Rate per 10 mm / 1rm |  |  |  | 1.68
| A | All Classes pipes :
| i | 63 mm dia pipe
Weight of 1m length = (0.468+0.666+1.01)/3 =0.715 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 6.3 | 1.68 | 10.58
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 10.58
| ii | 75 mm dia pipe
Weight of 1m length = (0.655+0.923+1.439)/3 =1.005 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 7.5 | 1.68 | 12.6
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 12.6
| iii | 90 mm dia pipe
Weight of 1m length = (0.924+1.321+2.032)/3 =1.426 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 9 | 1.68 | 15.12
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 15.12
| iv | 110 mm dia pipe
Weight of 1m length = (1.323+1.902+3.062)/3 =2.096 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 11 | 1.68 | 18.48
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 18.48
| v | 125 mm dia pipe
Weight of 1m length = (1.722+2.511+3.929)/3 =2.72 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 12.5 | 1.68 | 21
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 21
| vi | 140 mm dia pipe
Weight of 1m length = (2.144+3.116+4.905)/3 =3.388 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 14 | 1.68 | 23.52
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 23.52
| vii | 160 mm dia pipe
Weight of 1m length = (2.799+4.012+6.414)/3 =4.408 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 16 | 1.68 | 26.88
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 26.88
| viii | 180 mm dia pipe
Weight of 1m length = (3.581+5.134+8.092)/3 =5.602 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 18 | 1.68 | 30.24
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 30.24
| ix | 200 mm dia pipe
Weight of 1m length = (4.331+6.351+10.001)/3 =6.894 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 20 | 1.68 | 33.6
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 33.6
| x | 225 mm dia pipe
Weight of 1m length = (5.511+7.975+12.675)/3 =8.72 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 22.5 | 1.68 | 37.8
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 37.8
| xi | 250 mm dia pipe
Weight of 1m length = (6.674+9.886+15.666)/3 =10.742 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 25 | 1.68 | 42
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 42
| xii | 280 mm dia pipe
Weight of 1m length = (8.453+12.404+19.616)/3 =13.491 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 28 | 1.68 | 47.04
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 47.04
| xiii | 315 mm dia pipe
Weight of 1m length = (10.682+15.723+24.732)/3 =17.046 kgs
|  | (a) Labour charges for laying, jointing & testing | rm | 31.5 | 1.68 | 52.92
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per metre a+b |  |  |  | 52.92 |  |  |  | 67.2
[7 empty] | 355mm | 35.5 | 1.68 | 59.64
PHE-LJHE-12 | 12 | Laying and jointing of HDPE pipes by butt fusion welding as per IS:7634 – part-II/1975 as amended from time to time to the alignment and gradient and testing the pipeline to the required pressure. |  |  |  |  | Rates given in SSR page no.41&42 |  |  |  | HDPE PIPES
Note : Specialized labour is needed for execution of laying & jointing for HDPE Pipes with buttfusion welding technique as per IS Specification.
| i | 63 mm Dia
Taking output : Length - 480 m ; Joints - 40 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 4 | 350 | 1400
Jointing
|  | Fitter | day | 1 | 400 | 400
|  | Mazdoor | day | 2 | 350 | 700
Testing
|  | Fitter | day | 1 | 400 | 400
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 4005
(b) Machinery
|  | Hirecharges of Generator Set & Hydraulic Testing Equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 4 | 45 | 180
|  | Diesel | Lt | 8 | 36 | 288
|  | Water for Testing | Lt | 1496.2777 | 0.077 | 115.21 | incl.transportation
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 5788.21
|  | Rate per RM =d/480 |  |  |  | 12.06 | Go for | SSR Rate
| ii | 75 mm Dia
Taking output : Length - 456 m ; Joints - 38 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 4 | 350 | 1400
Jointing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 4015
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 4 | 33 | 132
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 2014.5463 | 0.077 | 155.12
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 5990.44
|  | Rate per RM =d/456 |  |  |  | 13.14 |  | SSR Rate
| iii | 90 mm Dia
Taking output : Length - 432 m ; Joints - 36 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 5 | 350 | 1750
Jointing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 4365
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 5 | 33 | 165
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 2748.2653 | 0.077 | 211.62
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 6429.94
|  | Rate per RM =d/432 |  |  |  | 14.88 |  | SSR Rate
| iv | 110 mm Dia
Taking output : Length - 384 m ; Joints - 32 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 6 | 350 | 2100
Jointing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 4715
(b) Machinery
|  | Hirecharges of Generator Set & Hydraulic Testing Equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 6 | 33 | 198
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 3649.274 | 0.077 | 280.99
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 6882.31
|  | Rate per RM =d/384 |  |  |  | 17.92 |  | SSR Rate
| v | 125 mm Dia
Taking output : Length - 348 m ; Joints - 29 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 7 | 350 | 2450
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 3 | 350 | 1050
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 5820
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 7 | 33 | 231
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 4270.6025 | 0.077 | 328.84
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 8068.16
|  | Rate per RM =d/348 |  |  |  | 23.18 |  | SSR Rate
| vi | 140 mm Dia
Taking output : Length - 300 m ; Joints - 25 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 7 | 350 | 2450
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 3 | 350 | 1050
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 5820
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 8 | 33 | 264
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 4618.1412 | 0.077 | 355.6
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 8127.92
|  | Rate per RM =d/300 |  |  |  | 27.09 |  | SSR Rate
| vii | 160 mm Dia
Taking output : Length - 303 m ; Joints - 25 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 7 | 350 | 2450
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 4 | 350 | 1400
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 6170
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 9 | 33 | 297
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 6092.1765 | 0.077 | 469.1
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 8624.42
|  | Rate per RM =d/303 |  |  |  | 28.46 |  | SSR Rate
| viii | 180 mm Dia
Taking output : Length - 240 m ; Joints - 20 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 8 | 350 | 2800
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 4 | 350 | 1400
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total Labour |  |  |  | 6520
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 10 | 33 | 330
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 6107.2561 | 0.077 | 470.26
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 9008.58
|  | Rate per RM =d/240 |  |  |  | 37.54 |  | SSR Rate
| ix | 200 mm Dia
Taking output : Length - 240 m ; Joints - 20 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 10 | 350 | 3500
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 6 | 350 | 2100
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 7920
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 11 | 33 | 363
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 7539.8224 | 0.077 | 580.57
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 10551.89
|  | Rate per RM =d/240 |  |  |  | 43.97 |  | SSR Rate
| x | 225 mm Dia
Taking output : Length - 216 m ; Joints -18 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 10 | 350 | 3500
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 6 | 350 | 2100
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 7920
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 12 | 33 | 396
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 8946.176 | 0.077 | 688.86
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 10693.18
|  | Rate per RM =d/216 |  |  |  | 49.51 |  | SSR Rate
| xi | 250 mm Dia
Taking output : Length - 216 m ; Joints - 18 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 11 | 350 | 3850
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 6 | 350 | 2100
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 8270
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 13 | 33 | 429
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 10602.8752 | 0.077 | 816.42
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 11203.74
|  | Rate per RM =d/216 |  |  |  | 51.87 |  | SSR Rate
| xii | 280 mm Dia
Taking output : Length - 192 m ; Joints - 16 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 12 | 350 | 4200
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 6 | 350 | 2100
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 8620
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 14 | 33 | 462
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 11822.4415 | 0.077 | 910.33
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 11680.65
|  | Rate per RM =d/192 |  |  |  | 60.84 |  | SSR Rate
| xiii | 315 mm Dia
Taking output : Length - 180 m ; Joints - 15 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 12 | 350 | 4200
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 6 | 350 | 2100
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 8620
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 15 | 33 | 495
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 14027.6039 | 0.077 | 1080.13
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 11883.45
|  | Rate per RM =d/180 |  |  |  | 66.02 |  | SSR Rate
| xiv | 355 mm Dia
Taking output : Length - 144 m ; Joints - 12 Nos
(a) Labour
For lowering / sub surface transport
|  | Mazdoor | day | 14 | 350 | 4900
Jointing
|  | Fitter | day | 2 | 405 | 810
|  | Mazdoor | day | 8 | 350 | 2800
Testing
|  | Fitter | day | 1 | 405 | 405
|  | Mazdoor | day | 2 | 350 | 700
|  | Supervisor | day | 1 | 405 | 405
|  | Total |  |  |  | 10020
(b) Machinery
|  | Hire charges of Generator Set & Hydraulic testing equipment | day | 1 | 1200 | 1200
(c) Material
|  | Kerosene | Lt | 16 | 33 | 528
|  | Diesel | Lt | 8 | 61.04 | 488.32
|  | Water for Testing | Lt | 14253.0917 | 0.077 | 1097.49
|  | Transport | day | 1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | (d) Total (a+b+c) |  |  |  | 13333.81
|  | Rate per RM =d/144 |  |  |  | 92.6 |  | SSR Rate
PHE-LJSW-13 | 13 | Lowering and laying in ready made trench true to alignment and gradient, jointing, and testing of stone ware pipes including cost of jointing material such as cement mortar (1:1) proportion and hemp yarn but excluding cost and conveyance of pipe. (Reference to specifications BIS No. 6530/72) |  |  |  |  | NOT UPDATED |  |  | STONE WARE PIPES
Detail cost for 30 meters
| i | 100 mm dia
(a) Labour
|  | Mason 1st class | day | 0.6 | 515 | 309
|  | Mason 2nd class | day | 1.4 | 400 | 560
|  | Man mazdoor | day | 3 | 350 | 1050
|  | Woman mazdoor (Water carrier) | day | 1 | 350 | 350
b) Material
|  | 100 mm dia SW pipe 60cm long | each/rm | 50
|  | Cement for 50 joints =0.045 cum | t/kg | 0.065
|  | Sand = 0.045 cum | cum | 0.045
|  | Spun yarn = 0.09x50=4.50 | kgs | 4.5
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| ii | 150 mm dia
(a) Labour
|  | Mason 1st class | day | 0.9 | 224 | 201.6
|  | Mason 2nd class | day | 2.1 | 206 | 432.6
|  | Man mazdoor | day | 4 | 170 | 680
|  | Woman mazdoor (Water carrier) | day | 1 | 170 | 170
b) Material
|  | 150 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.097
|  | Sand = 0.045 cum | cum | 0.068
|  | Spun yarn = 0.09x50=4.50 | kgs | 9
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| iii | 200 mm dia
(a) Labour
|  | Mason 1st class | day | 1.05 | 224 | 235.2
|  | Mason 2nd class | day | 2.45 | 206 | 504.7
|  | Man mazdoor | day | 4.5 | 170 | 765
|  | Woman mazdoor (Water carrier) | day | 1.25 | 170 | 212.5
b) Material
|  | 200 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.13
|  | Sand = 0.045 cum | cum | 0.091
|  | Spun yarn = 0.09x50=4.50 | kgs | 12
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| iv | 230 mm dia
(a) Labour
|  | Mason 1st class | day | 1.2 | 224 | 268.8
|  | Mason 2nd class | day | 2.8 | 206 | 576.8
|  | Man mazdoor | day | 5 | 170 | 850
|  | Woman mazdoor (Water carrier) | day | 1.5 | 170 | 255
b) Material
|  | 230 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.146
|  | Sand = 0.045 cum | cum | 0.102
|  | Spun yarn = 0.09x50=4.50 | kgs | 13.5
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| v | 250 mm dia
(a) Labour
|  | Mason 1st class | day | 1.35 | 224 | 302.4
|  | Mason 2nd class | day | 3.15 | 206 | 648.9
|  | Man mazdoor | day | 5.5 | 170 | 935
|  | Woman mazdoor (Water carrier) | day | 1.5 | 170 | 255
b) Material
|  | 250 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.162
|  | Sand = 0.045 cum | cum | 0.113
|  | Spun yarn = 0.09x50=4.50 | kgs | 15
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| vi | 300 mm dia
(a) Labour
|  | Mason 1st class | day | 1.5 | 224 | 336
|  | Mason 2nd class | day | 3.5 | 206 | 721
|  | Man mazdoor | day | 6 | 170 | 1020
|  | Woman mazdoor (Water carrier) | day | 1.5 | 170 | 255
b) Material
|  | 300 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.194
|  | Sand = 0.045 cum | cum | 0.136
|  | Spun yarn = 0.09x50=4.50 | kgs | 18
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| vii | 350 mm dia
(a) Labour
|  | Mason 1st class | day | 1.65 | 224 | 369.6
|  | Mason 2nd class | day | 3.85 | 206 | 793.1
|  | Man mazdoor | day | 7 | 170 | 1190
|  | Woman mazdoor (Water carrier) | day | 1.75 | 170 | 297.5
b) Material
|  | 350 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.225
|  | Sand = 0.045 cum | cum | 0.159
|  | Spun yarn = 0.09x50=4.50 | kgs | 21
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| viii | 400 mm dia
(a) Labour
|  | Mason 1st class | day | 1.8 | 224 | 403.2
|  | Mason 2nd class | day | 4.2 | 206 | 865.2
|  | Man mazdoor | day | 8 | 170 | 1360
|  | Woman mazdoor (Water carrier) | day | 1.75 | 170 | 297.5
b) Material
|  | 400 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.256
|  | Sand = 0.045 cum | cum | 0.181
|  | Spun yarn = 0.09x50=4.50 | kgs | 24
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
| ix | 450 mm dia
(a) Labour
|  | Mason 1st class | day | 2.1 | 224 | 470.4
|  | Mason 2nd class | day | 4.9 | 206 | 1009.4
|  | Man mazdoor | day | 10 | 170 | 1700
|  | Woman mazdoor (Water carrier) | day | 2 | 170 | 340
b) Material
|  | 450 mm dia SW pipe 60cm long | each | 50
|  | Cement for 50 joints =0.045 cum | t | 0.293
|  | Sand = 0.045 cum | cum | 0.204
|  | Spun yarn = 0.09x50=4.50 | kgs | 27
(c) Total = a+b
(d) Add for water charges @ 1% on Labour & Testing Charges
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 30 m (e+f)
Rate per metre = g/30
PHE-CISP-14(sub_analysis) | 13 | Sub Analysis :
|  | Labour charges for laying in position S&S or flanged C.I. specials such as tees, bends, collars tapers and caps etc | [7 empty] | CI SPECIALS
10 No. Tees of 200x150mm dia
Weight = 10x70kgs = 700 kgs
(a) Labour
|  | Plumber 1st class | day | 0.465 | 540 | 251.1
|  | Plumber 2nd class | day | 1.094 | 425 | 464.95
|  | Man mazdoor | day | 2.48 | 400 | 992
|  | Cost for 700 kgs |  |  |  | 1708.05
|  | Cost for 1kg |  |  |  | 2.44
PHE-CISV-15 | 15 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) excluding cost of bolts, nuts, rubber insertion, sluice valve and tail pieces | [7 empty] | SLUICE VALVES CI
Details of cost for 1No
| i | 80 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - Weight (32.3+34.1+40)/3=35.47 | kgs | 35.47 | 2.44 | 86.54
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 86.54
| ii | 100 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - Weight (44.3+47+50)/3=47.1 | kgs | 47.1 | 2.44 | 114.92
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 114.92
| iii | 125 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - Weight (56.3+59+70)/3=61.77 | kgs | 61.77 | 2.44 | 150.71
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 150.71
| iv | 150 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (72.5+77+90)/3=79.83 | kgs | 79.83 | 2.44 | 194.78
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 194.78
| v | 200 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (121.5+128.6+145)/3=131.7 | kgs | 131.7 | 2.44 | 321.34
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 321.34
| vi | 250 mm dia meter
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (179.9+186.6+195)/3=187.16 | kgs | 187.16 | 2.44 | 456.67
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 456.67
| vii | 300 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (242.4+257+300)/3=266.46 | kgs | 266.46 | 2.44 | 650.16
|  | (g) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per 1 Sluice valve |  |  |  | 650.16
| viii | 350 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (430+470)/2=450 | kgs | 450 | 2.44 | 1098
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 1098
| ix | 400 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (525+580)/2=552.5 | kgs | 552.5 | 2.44 | 1348.1
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 1348.1
| x | 450 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (635+810)/2=722.5 | kgs | 722.5 | 2.44 | 1762.9
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 1762.9
| xi | 500 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (775+900)/2=837.5 | kgs | 837.5 | 2.44 | 2043.5
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 2043.5
| xii | 600 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (1220+1625)/2=1422.5 | kgs | 1422.5 | 2.44 | 3470.9
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 3470.9
700 mm dia meter
(a) Labour
|  | Labour for laying Sluice Valve with cap, with hand wheel & reflex valves - (1220+1625)/2=1422.5 | kgs | 1422.5 | 2.44 | 3470.9
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 3470.9
PHE-DAAV-16 | 16 A | Providing and fixing double acting air valves including boring the main threading the bore and fixing nipple etc.,excluding the cost of rubber insertions, bolts & nuts, air valve & flanged tail pieces complete
Details of cost for each
| i | 50 mm dia meter
(a) Labour
|  | Labour for laying air valve | kgs | 28.336 | 2.44 | -37
|  | Plumber 2nd class | day | 0.18 | 400 | 72
|  | Man mazdoor | day | 0.18 | 350 | 63
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each valve |  |  |  | 98 | As per SSR pg.42
| 16 B | Labour charges for fixing Air valves including boring the mains and threading the bore fixing nipple etc., complete. | [7 empty] | AIR VALVES
Unit each
| i | 40 mm dia
(a) Labour
|  | Lowering charges for air valve | kgs | 27 | 2.44 | 65.88
Boring main & threding etc
|  | Plumber 2nd class | day | 0.14 | 400 | 56
|  | Man mazdoor | day | 0.14 | 350 | 49
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each valve |  |  |  | 170.88
| ii | 25 mm dia
(a) Labour
|  | Lowering charges for air valve | kgs | 20 | 2.44 | 48.8
Boring main & threding etc
|  | Plumber 2nd class | day | 0.11 | 400 | 44
|  | Man mazdoor | day | 0.11 | 350 | 38.5
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each valve |  |  |  | 131.3
PHE-SFHD-17 | 17 | Providing and fixing spindle fire hydrant with 65 mm outlet. Complete with bolts, nuts, and rubber insertion etc. complete but excluding cost of Materials.
Details of cost for 1fire hydrants
| i | 65 mm dia
(a) Labour
|  | Plumber 1st class | day | 0.75 | 224 | 168
|  | Plumber 2nd class | day | 1.75 | 206 | 360.5
|  | Man mazdoor | day | 4 | 170 | 680
|  | Overheads & Contractors Profit |  |  |  | 0
Rate per each fire hydrant
Note : For other sizes proportionately allow the Data.
PHE-DSFH-18 | 18 | Dismantling of spindle fire hydrant including stacking of useful materials within 50m lead
Details of cost for 10 Nos
65 mm dia
(a) Labour
|  | Fitter 1st class | day | 0.75 | 224 | 168
|  | Fitter 2nd class | day | 1.75 | 206 | 360.5
|  | Man mazdoor | day | 4 | 170 | 680
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate per each |  |  |  | 1208.5
PHE-URCI-19 | 19 | Uprooting of C.I. pipes by melting lead, loosening the joints, separating the pipes, hoisting and keeping within a lead of 10 metres but excluding earth work excavation and refilling
Details of cost for 40.26 m
| i | 80mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 0.5 | 206 | 103
|  | Man mazdoor | day | 4 | 170 | 680
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 0.373 | 300 | 111.9
|  | Kerosene oil | litre | 0.379 | 25 | 9.47
|  | (c) Total = a+b |  |  |  | 904.37
|  | (d) Overheads & Contractors Profit |  |  |  | 0
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| ii | 100mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 0.63
|  | Man mazdoor | day | 4.5 | 170 | 765
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 0.466
|  | Kerosene oil | litre | 0.379 | 25 | 9.47
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| iii | 125mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 0.76
|  | Man mazdoor | day | 5 | 170 | 850
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 0.559
|  | Kerosene oil | litre | 0.562 | 25 | 14.05
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| iv | 150mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 0.83
|  | Man mazdoor | day | 5.5 | 170 | 935
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 0.663
|  | Kerosene oil | litre | 0.568 | 25 | 14.2
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| v | 200mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 1.1
|  | Man mazdoor | day | 6.5 | 170 | 1105
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 0.84
|  | Kerosene oil | litre | 0.757 | 25 | 18.92
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| vi | 250mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 1.3
|  | Man mazdoor | day | 7.5 | 170 | 1275
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.026
|  | Kerosene oil | litre | 1.1365 | 25 | 28.41
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| vii | 300mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 1.5
|  | Man mazdoor | day | 8.5 | 170 | 1445
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.12
|  | Kerosene oil | litre | 1.515 | 25 | 37.87
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| viii | 350mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 1.75
|  | Man mazdoor | day | 9.5 | 170 | 1615
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.231
|  | Kerosene oil | litre | 1.515 | 25 | 37.87
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| ix | 400mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 2
|  | Man mazdoor | day | 10.5 | 170 | 1785
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.306
|  | Kerosene oil | litre | 1.894 | 25 | 47.35
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| x | 450mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 2.25
|  | Man mazdoor | day | 11.5 | 170 | 1955
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.4
|  | Kerosene oil | litre | 2.273 | 25 | 56.82
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| xi | 500mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 2.5
|  | Man mazdoor | day | 12.5 | 170 | 2125
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.492
|  | Kerosene oil | litre | 2.652 | 25 | 66.3
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
| xii | 600mm dia metre
(a) Labour
|  | Assistant fitter(plumber 2nd class) | day | 3
|  | Man mazdoor | day | 14.5 | 170 | 2465
b) Material
For breacking lead coulked joints, melting lead etc.,
|  | Fuel wood | q | 1.58
|  | Kerosene oil | litre | 3.41 | 25 | 85.25
(c) Total = a+b
(d) Overheads & Contractors Profit
(e) Cost for 40.26 m (c+d)
Rate per each m = e/40.26
PHE-URRC-20 | 20 | Uprooting of R.C.C. Pipes including breaking the collars, loosing the joint, scraping the pipe, hoisting and keeping within a lead of 10 M but excluding earthwork excavation and refilling
Taking output 10.00 Rmt
| i | 100mm dia
(a) Labour
|  | Fitter 2nd class | day | 0.1 | 206 | 20.6
|  | Man mazdoor | day | 0.4 | 170 | 68
|  | Women mazdoor | day | 0.45 | 170 | 76.5
(b) Overheads & Contractors Profit
(c) Cost for 10 Rmt (a+b)
Rate per each Rmt = c/10
| ii | 150mm dia
(a) Labour
|  | Fitter 2nd class | day | 0.1 | 206 | 20.6
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.56 | 170 | 95.2
(b) Overheads & Contractors Profit
(c) Cost for 10 Rmt (a+b)
Rate per each Rmt = c/10
| iii | 225mm dia
(a) Labour
|  | Fitter 2nd class | day | 0.1 | 206 | 20.6
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.67 | 170 | 113.9
(b) Overheads & Contractors Profit
(c) Cost for 10 Rmt (a+b)
Rate per each Rmt = c/10
| iv | 300mm dia
(a) Labour
|  | Fitter 2nd class | day | 0.1 | 206 | 20.6
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.79 | 170 | 134.3
(b) Overheads & Contractors Profit
(c) Cost for 10 Rmt (a+b)
Rate per each Rmt = c/10
PHE-URSW-21 | 21 | Uprooting of old S.W. pipes including breaking of joints and bed concrete stacking of useful materials near the site with in 50m lead and disposal of un serviceable materials in to municipal dumps excluding the cost of earth work excavation. (Reference to specifications BIS No.)
Details of cost for 10 m
| i | 100mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.36 | 170 | 61.2
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| ii | 150mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.45 | 170 | 76.5
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| iii | 200mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.51 | 170 | 86.7
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| iv | 230mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.54 | 170 | 91.8
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| v | 250mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.57 | 170 | 96.9
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| vi | 300mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.63 | 170 | 107.1
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| vii | 350mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.49 | 170 | 83.3
|  | Women mazdoor | day | 0.69 | 170 | 117.3
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| viii | 400mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.66 | 170 | 112.2
|  | Women mazdoor | day | 0.75 | 170 | 127.5
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| ix | 450mm dia metre
(a) Labour
|  | Man mazdoor | day | 0.66 | 170 | 112.2
|  | Women mazdoor | day | 0.81 | 170 | 137.7
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
PHE-URGI-22 | 22 | Removing old G.I.pipes and specials / fittings and cleaning, scraping the pipes, hoisting and keeping with in 50m lead but excluding earth work excavation of trenches and refilling
Details of cost for 10 m
| i | 15 to 40mm dia
(a) Labour
|  | Plumber | day | 0.13 | 206 | 26.78
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
| ii | Above 40mm dia
(a) Labour
|  | Plumber | day | 0.26 | 206 | 53.56
(b) Overheads & Contractors Profit
(c) Cost for 10 m (a+b)
Rate per each m =c/10
PHE-CCIP-23 | 23 | Cutting C.I. / D.I. pipes without water in mains
Details of cost for one cutting
| i | 80 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.06
|  | Man mazdoor | day | 0.06 | 170 | 10.2
(b) Overheads & Contractors Profit
Rate per each m
| ii | 100 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.08
|  | Man mazdoor | day | 0.08 | 170 | 13.6
(b) Overheads & Contractors Profit
Rate per each m
| iii | 125 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.11
|  | Man mazdoor | day | 0.11 | 170 | 18.7
(b) Overheads & Contractors Profit
Rate per each m
| iv | 150 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.15
|  | Man mazdoor | day | 0.15 | 170 | 25.5
(b) Overheads & Contractors Profit
Rate per each m
| v | 200 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.2
|  | Man mazdoor | day | 0.2 | 170 | 34
(b) Overheads & Contractors Profit
Rate per each m
| vi | 250 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.25
|  | Man mazdoor | day | 0.25 | 170 | 42.5
(b) Overheads & Contractors Profit
Rate per each m
| vii | 300 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.3
|  | Man mazdoor | day | 0.3 | 170 | 51
(b) Overheads & Contractors Profit
Rate per each m
| viii | 350 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.35
|  | Man mazdoor | day | 0.35 | 170 | 59.5
(b) Overheads & Contractors Profit
Rate per each m
| ix | 400 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.4
|  | Man mazdoor | day | 0.4 | 170 | 68
(b) Overheads & Contractors Profit
Rate per each m
| x | 450 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.45
|  | Man mazdoor | day | 0.45 | 170 | 76.5
(b) Overheads & Contractors Profit
Rate per each m
| xi | 500 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.5
|  | Man mazdoor | day | 0.5 | 170 | 85
(b) Overheads & Contractors Profit
Rate per each m
| xii | 600 mm dia
(a) Labour
|  | Asst. Fitter / Plumber 2nd class | day | 0.6
|  | Man mazdoor | day | 0.6 | 170 | 102
(b) Overheads & Contractors Profit
Rate per each m
PHE-DTCI-24 | 24 | Drilling and tapping C.I./D.I. main and fixing brass screw down ferrule and C.I.mouth cover.(Labour charges only)
Details of cost for one no
| i | 15 mm dia
(a) Labour
|  | Plumber | day | 0.13 | 206 | 26.78
(b) Overheads & Contractors Profit
Rate per each m
| ii | 20 mm dia
(a) Labour
|  | Plumber | day | 0.15 | 206 | 30.9
(b) Overheads & Contractors Profit
Rate per each m
| iii | 25 mm dia
(a) Labour
|  | Plumber | day | 0.17 | 206 | 35.02
(b) Overheads & Contractors Profit
Rate per each m
PHE-SHST-25 | 25 | Shoring and strutting of trenches for water and sewer lines
| (A) | Single staging from 0’ to 8’-0” ( 0 to 2.5 Metre)
Depth not exceeding 1.5 M
Details of cost for an area 30 M long and 1.5 M deep.
Area = 30 x 1.5 = 45 sqm
(a) Labour
|  | Carpenter 2nd class | day | 0.57
|  | Man mazdoor | day | 1.1 | 170 | 187
b) Material
|  | Polling boards and ballies | sqm
Requirement for 45 sqm :
|  | Polling Boards of 250 mm x 35 mm (40 x 1.5 x 0.25 x 0.038) | cum
|  | Ballies 125 mm dia 1.5 mts long (60 x p x (0.125)2 / 4 x 1.5 | cum
Deduct–Credit for materials after use @ 80% of the cost of materials =0.8 x X
c) Machinery
Nil
Overheads & Contractors Profit
(d) Cost for 45 sqm (a+b+c)
Rate per each sqm = d/45
| (B) | Double staging from 8’ to 14 ( 2.5 to 4.5 Metre)
Depth not exceeding 1.5 M
Details of cost for an area 30 M long and 1.5 M deep.
Area = 30 x 1.5 = 45 Sqm
(a) Labour
|  | Carpenter 2nd class | day | 0.5
|  | Man mazdoor | day | 1.32 | 170 | 224.4
b) Material
|  | Polling boards and ballies | sqm
Requirement for 45 sqm :
|  | Polling Boards of 250 mm x 35 mm (40 x 1.5 x 0.25 x 0.038 = 0.57 cum) | cum | 0.11
|  | Ballies 125 mm dia 1.5 mts long (60 x p x (0.125)2 / 4 x 1.5 = 1.1 cum | cum | 0.22
Deduct – Credit for materials after use @ 80% of the cost of materials = 0.8 x X
c) Machinery
Nil
Overheads & Contractors Profit
(d) Cost for 45 sqm (a+b+c)
Rate per each sqm = d/45
| (C) | Triple staging beyond 14’ for every 2 meter (beyond 4.5 M)
Depth not exceeding 1.5 M.
Note : Add for every 2 Mts (difference of single and double staging) for staging beyond 4.5 mts.
PHE-BHLW-26 | 26 | Barricading, hoarding, lighting and watching etc., for water supply and sewerage works for trenches of depths upto 6’-0” (2 Meter) below G.L
Taking output 3 Rmt
Material
|  | Bamboos of 1 ½ ”dia 2.5 M long (5 ft c/c = 3 x 2.5) | rmt | 7.5
|  | Baboom of 1 ½ ”dia 3.66 M long (5 ft c/c = 3x 3.66) | rmt | 10.98
Cost of Bamboos
(a) Usage of Material 5 times. Thus Cost of Material taken as 20%
(b) Labour
|  | Man mazdoor | day | 0.5 | 170 | 85
(c) Sundries for Coir rope, nails, @ 1%
(d) Sundries for lighting and watching etc at 1%
Overheads & Contractors Profit
Cost for 3rmt (a+b+c+d)
Rate per each rmt = (a+b+c+d)/3
PHE-RCVS-27 | 27 | Providing RCC spun vent shaft with cowl 140 mm and 200 mm internal and external dia respectively at top, 300 and 450 mm internal and external dia respectively at bottom and 9.10m overall length. Bottom 1.25 m below ground level fixed in a pit 90cmx90cm x150 cm with cement concrete 1:4:8, 25cm in bed and minimum 20cm all-round with top 15cm in cement concrete 1:2:4. Junction of vent shaft and concrete grouted with cement mortar 1:1 including making connection with sewer manhole with 150 mm dia metre cement concrete pipe of required length complete as per standard design
Details of cost for one vent shaft
(a) Labour
|  | Mason 1st class | day | 0.75 | 224 | 168
|  | Mason 2nd class | day | 0.25 | 206 | 51.5
|  | Man mazdoor (bhandani) | day | 2 | 170 | 340
|  | Man mazdoor (beldar) | day | 2 | 170 | 340
b) Material
|  | RCC went shaft with cowl | each | 1
|  | RCC pipe 150 mm dia 0.50 m (NP-2 class) | m | 0.5
Cement Concrete 1:4:8(plain)
0.90 x 0.90 x 135 = 1.094 cum
|  | Less for shaft 22/7 x 4 x 0.452 x 1.1= 0.175cum = 0.919 cum | cum | 0.92
Cement Concrete 1:2:4 (plain)
0.90 x 0.90 x 0.15 = 0.122 cum
|  | Less for shaft 22/7x4 x 0.452 x 0.15= 0.024cum = 0.098 cum | cum | 0.1
(c) Total (a+b)
|  | (d) Add for water charges @ 1% on Labour & Testing Charges on Labour Charges |  | 1%
(e) Total = c+d
(f) Overheads & Contractors Profit
(g) Cost for 1 No = e+f
Well Sinking
PHE-WSNP-28 | 28 | Well sinking in sandy and other loose soils under water either by manual labour, divers or dredgers weighting the top of staining to assist sinking etc., including dewatering and other incidental charges such as hire charges for mechanical equipment etc., complete upto 4.0 m dia (For non perennial rivers) | [7 empty] | WELL SINKING NON PERENIAL
| i | Upto 2.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 105 | 350 | 36750
|  | (b) Total |  |  |  | 36750
|  | Rate per Rm = b/2 |  |  |  | 18375
| ii | 2.0 to 4.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 70 | 350 | 24500
|  | Sinkers | day | 35 | 480 | 16800
b) Machinery
|  | Hire charges for crane | hour | 16 | 1231.4 | 19702.4
|  | Hire charges for Air compressor | hour | 56 | 1174.6 | 65777.6
|  | Hire charges for Generator | hour | 56 | 842.2 | 47163.2
|  | Diesel | L | 70 | 61.04 | 4272.8
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 178216
|  | Rate per Rm = c/2 |  |  |  | 89108
| iii | 4.0 to 6.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 56 | 350 | 19600
|  | Sinkers | day | 35 | 480 | 16800
b) Machinery
|  | Hire charges for crane | hour | 56 | 1231.4 | 68958.4
|  | Hire charges for Air compressor | hour | 56 | 1174.6 | 65777.6
|  | Hire charges for Generator | hour | 56 | 842.2 | 47163.2
|  | Diesel | L | 105 | 61.04 | 6409.2
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 224708.4
|  | Rate per Rm = c/2 |  |  |  | 112354.2
| iv | 6.0 to 8.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 56 | 350 | 19600
|  | Sinkers | day | 35 | 480 | 16800
b) Machinery
|  | Hire charges for crane | hour | 56 | 1231.4 | 68958.4
|  | Hire charges for Air compressor | hour | 56 | 1174.6 | 65777.6
|  | Hire charges for Generator | hour | 56 | 842.2 | 47163.2
|  | Diesel | L | 140 | 61.04 | 8545.6
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 226844.8
|  | Rate per Rm = c/2 |  |  |  | 113422.4
| v | 8.0 to 10.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 64 | 350 | 22400
|  | Sinkers | day | 40 | 480 | 19200
b) Machinery
|  | Hire charges for crane | hour | 64 | 1231.4 | 78809.6
|  | Hire charges for Air compressor | hour | 64 | 1174.6 | 75174.4
|  | Hire charges for Generator | hour | 64 | 842.2 | 53900.8
|  | Diesel | L | 140 | 61.04 | 8545.6
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 258030.4
|  | Rate per Rm = c/2 |  |  |  | 129015.2
PHE-WSOW-29 | 29 | Sinking of RCC 12 m dia well in sandy soils, soft disintegrated rock, loamy and clayey soils etc; under water by manual or mechanical means including dewatering until the completion of sinking of the well to the required depth, the dummies of the weep holes pipes are opened for seepage of water into well, including all hire charges complete as per SS and as directed by the departmental officers (Open well excavation)
| i | Upto 2.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 168 | 350 | 58800
|  | (b) Total |  |  |  | 58800
|  | Rate per Rm = b/2 |  |  |  | 29400
| ii | 2.0 to 4.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 178 | 350 | 62300
|  | Crane Operator | day | 11 | 515 | 5665
b) Machinery
|  | Hire charges for crane | hour | 88 | 1231.4 | 108363.2
|  | Hire charges for Generator | hour | 88 | 842.2 | 74113.6
|  | Diesel | L | 440 | 61.04 | 26857.6
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 277299.4
|  | Rate per Rm = c/2 |  |  |  | 138649.7
| iii | 4.0 to 6.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 157 | 350 | 54950
|  | Sinkers | day | 48 | 480 | 23040
|  | Crane Operator | day | 12 | 515 | 6180
b) Machinery
|  | Hire charges for crane | hour | 96 | 1231.4 | 118214.4
|  | Hire charges for Air compressor | hour | 102 | 1174.6 | 119809.2
|  | Hire charges for Generator | hour | 96 | 842.2 | 80851.2
|  | Diesel | L | 1056 | 61.04 | 64458.24
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 467503.04
|  | Rate per Rm = c/2 |  |  |  | 233751.52
| iv | 6.0 to 8.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 195 | 350 | 68250
|  | Sinkers | day | 120 | 480 | 57600
|  | Crane Operator | day | 15 | 515 | 7725
b) Machinery
|  | Hire charges for crane | hour | 120 | 1231.4 | 147768
|  | Hire charges for Air compressor | hour | 124 | 1174.6 | 145650.4
|  | Hire charges for Generator | hour | 120 | 842.2 | 101064
|  | Diesel | L | 1334 | 61.04 | 81427.36
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 609484.76
|  | Rate per Rm = c/2 |  |  |  | 304742.38
| v | 8.0 to 10.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 272 | 350 | 95200
|  | Sinkers | day | 204 | 480 | 97920
|  | Crane Operator | day | 17 | 515 | 8755
b) Machinery
|  | Hire charges for crane | hour | 124 | 1231.4 | 152693.6
|  | Hire charges for Air compressor | hour | 124 | 1174.6 | 145650.4
|  | Hire charges for Generator | hour | 136 | 842.2 | 114539.2
|  | Diesel | L | 1344 | 61.04 | 82037.76
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 696795.96
|  | Rate per Rm = c/2 |  |  |  | 348397.98
| vi | 10.0 to 12.85 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 360 | 350 | 126000
|  | Sinkers | day | 288 | 480 | 138240
|  | Crane Operator | day | 24 | 515 | 12360
b) Machinery
|  | Hire charges for crane | hour | 192 | 1231.4 | 236428.8
|  | Hire charges for Air compressor | hour | 198 | 1174.6 | 232570.8
|  | Hire charges for Generator | hour | 160 | 842.2 | 134752
|  | Diesel | L | 2148 | 61.04 | 131113.92
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 1011465.52
|  | Rate per Rm = c/2.85 |  |  |  | 505732.76
PHE-WSPR-30 | 30 | Well sinking in sandy and other loose soils under water either by manual labour, divers or dredgers weighting the top of steining to assist sinking etc., including dewatering and other incidental charges such as hire charges for mechanical equipment etc., complete upto 7 m dia (In Perennial Rivers only) | [7 empty] | WELL SINKING PERENIAL
| i | Upto 2.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 32 | 350 | 11200
|  | Well sinkers | day | 64 | 480 | 30720
b) Machinery
|  | Hire charges of set of Helmets & Air circulating pipes / valves | day | 4 | 500 | 2000 |  | 500 | local observed rates
|  | Hire charges for crane | hour | 32 | 1231.4 | 39404.8
|  | Hire charges for compressors | hour | 32 | 1174.6 | 37587.2
|  | Diesel | L | 120 | 61.04 | 7324.8
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 128236.8
|  | Rate per Rm = c/2 |  |  |  | 64118.4
| ii | 2.0 to 4.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 40 | 350 | 14000
|  | Well sinkers | day | 80 | 480 | 38400
b) Machinery
|  | Hire charges of set of Helmets & Air circulating pipes / valves | day | 5 | 500 | 2500
|  | Hire charges for crane | hour | 40 | 1231.4 | 49256
|  | Hire charges for compressors | hour | 40 | 1174.6 | 46984
|  | Diesel | L | 150 | 61.04 | 9156
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 160296
|  | Rate per Rm = c/2 |  |  |  | 80148
| iii | 4.0 to 6.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 48 | 350 | 16800
|  | Well sinkers | day | 96 | 480 | 46080
b) Machinery
|  | Hire charges of set of Helmets & Air circulating pipes / valves | day | 6 | 500 | 3000
|  | Hire charges for crane | hour | 48 | 1231.4 | 59107.2
|  | Hire charges for compressors | hour | 48 | 1174.6 | 56380.8
|  | Diesel | L | 180 | 61.04 | 10987.2
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 192355.2
|  | Rate per Rm = c/2 |  |  |  | 96177.6
| iv | 6.0 to 8.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 56 | 350 | 19600
|  | Well sinkers | day | 112 | 480 | 53760
b) Machinery
|  | Hire charges of set of Helmets & Air circulating pipes / valves | day | 7 | 500 | 3500
|  | Hire charges for crane | hour | 56 | 1231.4 | 68958.4
|  | Hire charges for compressors | hour | 56 | 1174.6 | 65777.6
|  | Diesel | L | 210 | 61.04 | 12818.4
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 224414.4
|  | Rate per Rm = c/2 |  |  |  | 112207.2
| v | 8.0 to 10.0 m below G.L. :
(a) Labour
|  | Man mazdoor | day | 64 | 350 | 22400
|  | Well sinkers | day | 128 | 480 | 61440
b) Machinery
|  | Hire charges of set of Helmets & Air circulating pipes / valves | day | 8 | 500 | 4000
|  | Hire charges for crane | hour | 64 | 1231.4 | 78809.6
|  | Hire charges for compressors | hour | 64 | 1174.6 | 75174.4
|  | Diesel | L | 240 | 61.04 | 14649.6
|  | Overheads & Contractors Profit |  |  |  | 0
|  | c) Total |  |  |  | 256473.6
|  | Rate per Rm = c/2 |  |  |  | 128236.8
Note : This data shall be adopted for well sinking in perennial rivers. For other rivers, data available for 4.0 m dia infiltration well may be adopted for guidance
PHE-CCCP-31 | 31 | Curing of CC pavement for 21 days including cost and conveyance of water, labour charges, etc., complete
Areas Considered 3 . 5 x 100 mts = 350 sqm
Units = 1 sqm
Mud quantity is required = 14% of CC area x 5 cm
(a) Labour
|  | Man mazdoor (21 x 2). | day | 42 | 350 | 14700
b) Machinery
|  | Carting earth for 3 kms | cum | 2.45 | 37.55 | 92
|  | Hire charges for Water Drum (5 x 21 days) | each | 105 | 10 | 1050
c) Material
|  | Earth Work (100 x 3.5 x 14/100 x .05) | cum | 2.45 | 71.67 | 175.59
|  | Supply of Water (240 Lts / cum / day) | L | 18900 | 77 | 1455300
Overheads & Contractors Profit
|  | (d) Total = a+b+c |  |  |  | 1471317.59
|  | Rate per sqm =d/350 |  |  |  | 4203.7645
Note : 1. When Curing compound is used @ 1.97 kgs/cum, water requirement is 206 Lts / cum per 14 days.
2. This data is for urban areas only
PHE-CSHR-32 | 32 | Cutting sheet rock including stocking of excavated material.
Quality of sheet rock as per stock measurement = 36.53 cumm (taking out put = 36.53 cum)
(a) Labour
|  | Man mazdoor | day | 60 | 350 | 21000
b) Machinery
|  | Drilling of holes | each | 342
|  | Hire charges for JCB | hr | 3 |  | 0
|  | MS Nokkulu | each | 10
Overheads & Contractors Profit
|  | (c) Total = a+b |  |  |  | 21000
Rate per cum =c/36.53
PHE-EXRW-33 | 33 | Excavation in Hard Rock (blasting prohibited)
Excavation for roadway in hard rock (blasting prohibited) with rock breakers including breaking rock, loading in tippers and disposal with all lifts and lead upto 1000 metres, trimming bottom and side slopes in accordance with requirements of lines, grades and cross- sections as per Technical Specification Clause 302.3.5
| (A) | Manual Means
Unit = cum
Taking output = 1 cum
a) Labour
|  | Mate | day | -
|  | Mazdoor (Unskilled) | day | 1.1 | 350 | 385
|  | Chiseller (Hammer Man) | day | 1.5 | 400 | 600
|  | Blacksmith | day | 0.06 | 445 | 26.7
b) Machinery
|  | Tipper 5.5 cum capacity, 1 trip per hour | hour | 0.18 | 924.1 | 166.33
|  | Credit for excavated rock found suitable for use @ 50 per cent of excavated quantity | cum | 0.5
Sundries on Labour
|  | c&d) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per cum = (a+b+c+d) |  |  |  | 1178.03
Note : 1. Credit is considered for 50 per cent of quantity of work.
2. Loading for disposal will be done manually, being small quantity.
3. In case some rock is issued to contractor at site, the item of carriage shall be omitted to the extent of quantity issued to the Contractor.
| (B) | Mechanical Means
Unit = cum
Taking output = 1 cum
a) Labour
|  | Mate | day | -
|  | Mazdoor (Unskilled) | day | 0.289 | 350 | 101.15
b) Machinery
|  | Hydraulic excavator 0.9 cum with rock breaker attachment @ 6 cum per hour | hour | 0.167
|  | Tipper 5.5 cum capacity tipper, 1 trip per hour | hour | 0.18 | 924.1 | 166.33
|  | Credit for excavated rock found suitable for use @ 50 per cent of excavated quantity | cum | 0.5
Sundries on Labour
|  | c&d) Overheads & Contractors Profit |  |  |  | 0
|  | Rate per cum = (a+b+c+d) |  |  |  | 267.48
Note : 1. The quality and availability of rock shall be checked before affording credit.
2. In case some rock is issued to the contractor at site, the item of carriage shall be restricted/reduced to that extent.
3. Being small quantity, manual loading will be economical in this case and has been provided accordingly.
PHE-LUSS-34 | 34 | Loading or Unloading materials such as C.I / D.I Pipes, R.C.C. Pipes, P.V.C. pipes, A.C. Pressure pipes and Specials less than 300 mm upto 4 mts in length including stacking.
| i | C.I Pipes and Specials (load per truck =6.50 T)
Taking Output = 13.00 MT (Load for each Truck 6.5 MT)
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 13 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 163.1538
| ii | RCC Pipes and Collars (load per truck =7.205 T)
Taking Output = 14.41 MT
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 14.41 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 147.1895
| iii | AC Pipes and Collars (load per truck = 5.40 T)
Taking Output = 10.8 MT
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 10.8 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 196.3889
| iv | Stone ware pipes (load per truck = 5.40 T)
Taking Output = 10.8 MT
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 10.8 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 196.3889
PHE-LUMS-35 | 35 | Loading or unloading materials such as C.I / D.I. Pipes, stone ware pipes, R.C.C. pipes, A.C. Pressure pipes and specials from 300 mm to 600 mm dia upto 4 mts in length including stacking.
| i | C.I. / D.I. Pipes (load per truck = 5.5 T)
Taking Output = 11 MT
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 11 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 192.8182
| ii | RCC Pipes and Collars (load per truck =5.75 T)
Taking Output = 11.5 MT
a) Labour
|  | Man Mazdoor | day | 6 | 350 | 2100
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 21
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 11.5 MT |  |  |  | 2121
|  | Rate per MT |  |  |  | 184.4348
| iii | AC Pipes
Taking Output = 1MT
a) Labour
|  | Man Mazdoor | day | 0.7 | 350 | 245
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.45
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for MT |  |  |  | 247.45
| iv | Stone ware pipes
Taking Output = 1MT
a) Labour
|  | Man Mazdoor | day | 0.7 | 350 | 245
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.45
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for MT |  |  |  | 247.45
PHE-LUGS-36 | 36 | Loading or unloading materials such as CI / DI Pipes, A.C. pressure pipes less than 300 mm dia above 4.00 M in length including stacking
| i | C.I. / D.I. Pipes (load per truck = 8.46 T)
Taking Output = 1 MT
a) Labour
|  | Man Mazdoor | day | 0.71 | 350 | 248.5
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.485
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 1 MT |  |  |  | 250.985
| ii | AC Pipes (load per truck = 3.78 T)
Taking Output = 1MT
a) Labour
|  | Man Mazdoor | day | 0.79 | 350 | 276.5
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.765
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for MT |  |  |  | 279.265
PHE-LUBS-37 | 37 | Loading or Unloading materials such as C.I / D.I. Pipes, A.C. Pressure pipes from 300 to 600mm dia above 4.00 m including stacking
| i | AC Pipes (load per truck = 4.3 T)
Taking Output = 1 MT
a) Labour
|  | Man Mazdoor | day | 0.714 | 350 | 249.9
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.499
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for 1 MT |  |  |  | 252.399
| ii | C.I. Pipes (load per truck = 3.85 T)
Taking Output = 1MT
a) Labour
|  | Man Mazdoor | day | 0.78 | 350 | 273
|  | Add sundries at 1% towards Nylon rope, Tyres etc |  | 1% |  | 2.73
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Cost for MT |  |  |  | 275.73
PHE-CSRC-38 | 38 | Centering and scaffolding charges for R.C.C. members including all materials and labour charges for forming and dismantling
| A | For R.C.C. Elevated Service Reservoir of Staging upto 40 Ft. below G.W.L.
| i | Side wall straight surfaces:
Details cost for 15 M long and 1 M height wall
Surface area = 2 x 15 x 1 = 30 Sqm
a) Materials
i) Planks 33 mm thick
2 x 15 x 1 = 30.00 sqm
Add 5% wastage = 1.5
=31.50 sqm
|  | 31.50 x 0.038 = 1.197 Cum | cum | 1.197
ii) Batters – 75 x 50 mm
|  | 2 x 13 x 0.075 x 0.05 = 0.095 cum | cum | 0.095
iii) Ballies – 125 dia for strutting
ver 13 x 1.5 = 19.5
13 x 4.5 = 58.5
= 78.00
5% for wastage = 3.9
= 81.90
|  | 81.90 x π x 0.1252 / 4 =1.005 Cum | cum | 1.005
Assuming that timber shall become unserviceable after being used for 5 times
Cost for 5 times
Rate per 1 time
b) Labour
Labour charges for assembling, erection, dismantling and cleaning
|  | Carpenter 2nd class | day | 7.5
|  | Man Mazdoor | day | 6 | 350 | 2100
Sundries for nails etc
Overheads & Contractors Profit
c) Cost for 30 Sqm
Rate per sqm =c/30
| ii | Side walls curved surfaces
Considering 4 M internal dia and 1 Meter depth. Consider 30 mm thick.
Surface area:
Outside – π x 4.40 x 1.00 = 13.83 Sqm
Inside area = π x 4 x 1 = 12.57 Sqm
= 26.40 Sqm
a) Materials
i) Planks 33 mm
26.40 x 0.038 = 1.003 cum
Extra & Wastage @ 20% = 0.201 cum
|  | = 1.204 Cum | cum | 1.204
ii) Hattens – 75 x 38 mm
Inside – 2 x 25 x 0.50 x 0.075 x 0.075 = 0.1406
Outside – 2 x 28 x 0.50 x 0.075 x 0.175 = 0.1575
= 0.2981
Add 5% wastage = 0.0149
|  | = 0.3130 cum | cum | 0.313
iii) Ballion 125 mm dia
Inside – 25 x 1 = 25 m
Outside – 28 x 1 = 28 m
= 53.00 m
Add 5% wastage = 2.65 m
|  | 55.65 π x 0.1252 = 0.68 cum | cum | 0.68
Assuming that timber shall become unserviceable after being used for 5 times
Cost for 5 times
Rate per 1 time
b) Labour
Add labour charges for assembling, erection and dismantling etc., @ 1/6 cost of materia
c) Total
Overheads & Contractors Profit
c) Cost for 26.04 Sqm
Rate per sqm =c/26.04
| B | For Ground level works
| i | R.C.C. vertical wells of plane surface upto 3 meters height such as G.L. tanks clarifiers and sludge digestor etc,
Rate per Sqm (as arrived in item A (i) above)
| ii | R.C.C. Vertical walls of circular faces upto 3 meters height
Rate per Sqm (as arrived in item A (ii) above)
PHE-HSSG-39 | 39 | Hoisting of S.S. Girders in pump house etc.
Detail cost of S.S. Joist = 300 x 140 mm - 6 M long
Wt. 44.2 Kgs/M = 6 x 44.20 = 265.20 kgs
Tolerances @ 5% = 13.26 kgs
= 278.46 kgs
a) Labour
Labour for hoisting inn position:
|  | Mason 2nd class | day | 1 | 400 | 400
|  | Man Mazdoor | day | 2.75 | 350 | 962.5
|  | Total |  |  |  | 1362.5
|  | (b) Overheads & Contractors Profit |  |  |  | 0
|  | c) Cost for 278.46 Sqm |  |  |  | 2725
|  | Rate per sqm =c/278.46 |  |  |  | 9.786
Cost for 50 Kg
PHE-LCVS-40 | 40 | Labour charges for fixing ventilating shafts in sewerage scheme complete with all accessories
Unit – Each
a) Labour
|  | Mason 1st class | day | 0.15 | 515 | 77.25
|  | Mason 2nd class | day | 0.35 | 400 | 140
|  | Plumber 2nd Class | day | 0.6 | 400 | 240
|  | Man Mazdoor | day | 2 | 350 | 700
|  | Overheads & Contractors Profit |  |  |  | 0
|  | Rate |  |  |  | 1157.25
Note on C1023: rammohan:
Note on C1039: rammohan:
Note on C1055: rammohan:
Note on C1071: rammohan:
Note on C1087: rammohan:
Note on C1103: rammohan:
Note on C1119: rammohan:
Note on C1135: rammohan:
Note on C1151: rammohan:
Note on C1167: rammohan:
Note on C1183: rammohan:
Note on C1199: rammohan:
Note on C1226: rammohan:
Note on C1242: rammohan:
Note on C1258: rammohan:
Note on C1274: rammohan:
Note on C1290: rammohan:
Note on C1306: rammohan:
Note on C1322: rammohan:
Note on C1338: rammohan:
Note on C1354: rammohan:
Note on C1370: rammohan: